1. ------IND- 2019 0651 A-- EN- ------ 20191231 --- --- PROJET

Ordinance of the Provincial Government of …………, amending the 2014 Tyrol Gas, Heating and Climate Control Systems Ordinance

On the basis of Article 3(2) of the 2013 Tyrol Gas, Heating and Climate Control Systems Act, Provincial Law Gazette No 111/2013, last amended by the Act published in Provincial Law Gazette No 144/2018, the following is hereby decreed:

Article I

The 2014 Tyrol Gas, Heating and Climate Control Systems Ordinance, Provincial Law Gazette No 80/2014, as amended by the Ordinance published in Provincial Law Gazette No 9/2018, is amended as follows:

1. In § 2, the following provision is added after paragraph 5 as paragraph 6:

‘(6) For new buildings within the meaning of § 2(7) of the 2018 Tyrolean Building Code, Provincial Law Gazette No 28/2018, as amended, and for larger renovations within the meaning of § 2(27) of the 2018 Tyrolean Building Regulations, the use of solid fossil fuels under Annex 1 and liquid fossil fuels under Annex 2 in central heating systems is not permitted.’

2. § 3(7) and (8) read as follows:

‘(7) Heating and climate control systems are to be set up and operated in such a way as to avoid unacceptable noise pollution for neighbours. In particular, there is no unacceptable noise pollution if the A-weighted sound pressure level of the permanent noise caused by them at the property boundary in the open air to neighbouring properties that are not traffic areas under § 2(21) of the 2018 Tyrolean Building Regulations does not exceed the following dB values in the respective operating mode:

|  | Daytime 6:00 to 19:00 | Evening 19:00 to 22:00 | Night time 22:00 to 06:00 |
| --- | --- | --- | --- |
| Residential area | 40 dB | 35 dB | 30 dB |
| Mixed residential area or tourist area | 45 dB | 40 dB | 35 dB |
| Core area, agricultural and general mixed area | 50 dB | 45 dB | 40 dB |

In relation to special areas under § 43 of the 2016 Tyrolean Spatial Planning Act, Provincial Law Gazette No 101/2016, as amended, and in relation to built-up plots in open land under § 41 of the 2016 Tyrolean Spatial Planning Act, the dB values to be used are those for the building land with the type of use that comes closest to the intended use specified in the special area.

(8) The limit values specified in paragraph 7 may be exceeded if the base level determined at the property boundary in accordance with the latest technology is not increased by more than 3 dB.’

3. §28(2) reads as follows:

‘(2) This Ordinance governs the following areas:

a)	in accordance with the provisions of Directive 98/34/EC of the European Parliament and of the Council laying down a procedure for the provision of information in the field of technical standards and regulations and of rules on information society services, OJ 1998, L 204, p. 37, last amended by Regulation (EU) 1025/2012, OJ 2012 L 316, p. 12 (notification number 2013/0703/A) and

b)	in accordance with the provisions of Directive (EU) 2015/1535 laying down a procedure for the provision of information in the field of technical regulations and of rules on Information Society services, OJ 2015 L 241, p. 1 (Notification No XXXX/XXXX/X).’

Article II

This Ordinance shall enter into force on the day following its promulgation.