DRAFT PRESIDENTIAL DECREE

Regulation on the fire protection of buildings

Having regard to the provisions of:

- The provisions of Article 90 of Legislative Decree 8/1973 on the General Building Regulation (Government Gazette, Issue A’ No 124), as replaced by Article 43 paragraph 1 of Law 4262/2014 on the simplification of authorisation for the exercise of an economic activity and other provisions (GG Issue A’ No. 114).

- Commission Decision 2000/367/EC of 3 May 2000 implementing Council Directive 89/106/EEC as regards the classification of the resistance to fire performance of construction products and parts thereof (OJ L 133/6.6.2000, p. 26 et seq.).

- Regulation (EU) No 305/2011 of the European Parliament and of the Council of 9 March 2011 laying down harmonised conditions for the marketing of construction products and repealing Council Directive 89/106/EEC (OJ L 88/4.4.2011, p. 5 et seq.), as in force.

- Commission Delegated Regulation (EU) 2016/364 of 1 July 2015 on the classification of construction products based on the reaction-to-fire performance pursuant to Regulation (EU) No 305/2011 of the European Parliament and of the Council (OJ L 68/15.3.2016, p. 4 et seq.), as in force.

- The provisions of Article 90 of the Code of Law on Government and Government Bodies, ratified by the first Article of the Presidential Decree 63/2005 (A’ 98).

- Decision Υ 197/16-11-2016 of the Prime Minister delegating powers to the Alternate Minister for the Economy and Development, Alexandros Charitsis (Β’ 3722);

- Decision Υ 186/10-11-2016 of the Prime Minister delegating powers to the Alternate Minister of Interior Nikolaos Toska (Β’ 3671);

- The fact that the provisions of this decree shall not encumber the national budget.

- Opinion No 132/2017 of the Council of State, on a proposal from the Minister for the Environment and Energy and the Alternate Ministers for the Economy and Development and the Interior.

we hereby decide:

First Article

A ‘Building Fire Protection Regulation’ is issued as follows:

REGULATION
ON THE FIRE PROTECTION
OF BUILDINGS

# CHAPTER A: GENERAL PROVISIONS

## Article 1: Purpose of the Regulation

## Article 2: Scope

## Article 3: Definitions

## Article 4: Building classification according to their use

## Article 5: Escape routes

## Article 6: Structural fire protection

## Article 7: Active fire protection means

## Article 8: Standards – technical specifications – certificates

Article 1: Purpose of the Regulation

The Regulation on the fire protection of buildings lays down the requirements and the measures to be taken in buildings, in order to:

a) To protect the life and health of the people who are in them in the event of a fire.

b) To prevent the spread of fire from the area where it occurred in other areas of the building.

c) To prevent the transmission of fire from the area that occurred in the neighbouring and neighbouring properties as well as in neighbouring areas.

d) protect the buildings themselves and their contents.

The main purpose of the Regulation on the fire protection of buildings remains the safety of the public in case of fire, which is generally met by the adequate design of the building and its components, the installation of active means and systems, and the right choice of materials and equipment.

More precisely, the regulation lays down:

- All measures that protect the building against collapse due to fire, at least for as long as is necessary for its evacuation;

- minimum design requirements of escape routes permitting the rapid evacuation of the building and the secure exit of its users or their transition to another safe area or building, without suffering the consequences of smoke, toxic fumes or heat produced in case of fire;

- maximum permitted size of the building's fire compartments, so that the fire can be contained if possible in the area where it started;

- measures preventing the fire spreading to adjacent buildings;

- requirements on materials used in buildings in relation to their location in the building and the use of the building, in order to avoid the rapid spread of the fire;

- The active measures and fire protection systems that allow the timely detection of the fire, its stopping and the safe escape of the users of the building, providing them with the necessary evacuation time and fire protection.

The main factors that were taken into consideration for determining the aforementioned requirements and achieving the objectives of the regulation are the following:

a) the possible users of the building, their characteristics and their familiarity with the building;

b) the interaction between areas in terms of fire risk;

c) the way buildings are designed and constructed in Greece.

The Building Fire Protection Regulation, as a special regulation, contains security requirements that specify other general building design regulations, such as the Building or Building Regulation, and prevail over them, insofar as they regulate relevant issues.

The Fire Protection Regulation examines the building requirement of the fire safety of buildings and applies alongside the other building requirements of other regulations – special provisions.

The Regulation on the fire protection of buildings only refers to single sources of ignition and does not address cases of arson, sabotage, vandalism, terrorist attack, or other similar acts.

## Article 2: Scope

- The application of the Regulation on the fire protection of buildings is obligatory:

a) for buildings or parts of buildings constructed after its entry into force, when their uses fall in one of the categories mentioned in article 4 of this Chapter;

b) In the case of construction of functionally independent additions to existing buildings.

c) for buildings or parts of buildings that fell under the purpose and scope of the Chapter A of formerly applicable Presidential Decree 71/88 (A '32), for which a fire protection study had been prepared in accordance with its provisions and in which their use is changed after the entry into force of this Regulation, in whole or in part, and/or the addition of a functionally dependent building.

d) for buildings pre-existing the entry into force of the PD (Presidential Decree). 71/88 in which, after the entry into force of this Building Fire Protection Regulation, a change in their use as a whole takes place.

e) In the cases of functionally dependent additions with main use, in buildings erected before the validity of chapter A' of PD (Precedential Decree). 71/88, as long as they exceed 50% of the total area of main use areas of the existing building and at the same time have an area of over 300 sq.m.

f) In the substations of the electricity distribution company that are erected after the validity of the present, with the said service being responsible for its correct application, in the specific areas of its property.

- In all other cases where a fire protection analysis is required for existing buildings, the relevant Provisions on fire fighting apply, in their current version.

- The aforementioned conditions do not apply to buildings that have been designated as monuments or as traditional or protected buildings by the responsible Ministries, and whose uses define the fire protection requirements according to the relevant Provision on fire fighting, with the possibility of derogations through the enforcement of additional compensatory fire protection measures by the responsible fire department, if this is necessary in order to protect the special elements on which their designation as protected buildings is based. The aforementioned reasons are included in a technical report prepared by the responsible engineer, which is submitted to the fire department after having been approved by the Ministry responsible for the designation of the building.

- Special provisions related to the installation of active fire protection means for specific categories of buildings or uses apply in addition to the requirements of this Regulation.

- In case of buildings that fall under categories (C) Public assemblage, (J) Industry - Small crafts industry and (K) Storage of article 4 of this Regulation, and that are of large scale and have a particular form and function, and to which the full application of the provisions on passive fire protection included in the general and specific articles of this Regulation has proved impossible, a passive fire protection analysis can be prepared, by way of derogation, increasing the passive and active means of fire protection in such a way that an equivalent degree of fire safety of the building and safety of the public is guaranteed.

This analysis shall be approved by a five member committee comprising of specialist scientists and representatives of the public and private sector, after a relevant reasoned proposal has been submitted by the entity that is responsible for the functionality of the building.

The application of the said derogation to the specific building as well as the establishment of the committee are subject to a common decision by the Minister of Environment and Energy and other responsible Ministers, after a reasoned proposal has been submitted by the responsible Department of the Ministry of Environment and Energy.

The scope of this Regulation is shown in Table 1.

Table 1: Scope of regulations on fire protection

| REGULATIONS ON FIRE PROTECTION | SCOPE | CLARIFICATIONS - OBSERVATIONS |  |
| --- | --- | --- | --- |
| Regulation on the fire protection of buildings | New buildings | Buildings or parts of buildings constructed under a building permit for which an application is submitted after the entry into force of this Regulation |  |
|  | Functionally independent additions to existing buildings | Treated as new buildings due to their autonomy |  |
|  | Existing buildings built after 17/2/1989 | Change of use or addition to buildings that have been the object of analysis according to P.D. 71/88 |  |
|  | Hotels built before 17/3/1988 |  |  |
|  | Buildings built before 17/2/1989 (except hotels) | Complete change of use | Additions to existing buildings covering >50% of the plot that have a surface >300 m2 |
| Fire fighting provisions - Measures | Buildings built before 17/2/1989 (except hotels) | According to their use |  |
|  | Monuments, protected buildings, traditional buildings | According to their use and with the possibility for derogations |  |

## Article 3: Definitions

For the purposes of this Regulation, the following definitions apply:

Cul-de-sac A common corridor (or area in a storey) that does not lead to an emergency exit, obliging the user to move to the opposite direction in order to escape.

Patio: The covered or uncovered part of the plot or of the building that is completely surrounded by the building or buildings in the plot, which is not a closed shaft of any vertical communication element of the building (stairway, escalator or lift), nor a passage of any kind of electromechanical installation.

Non-combustible building material: Low flammability material, which meets the criteria of the respective combustion test.

Integrity in fire: The ability of a building element when exposed to fire on one side to prevent flames and hot gases from passing through and reaching the other non exposed side for a specified time in a typical fire resistance test.

Fire-fighters lift: Lift that is specifically designed and constructed in order to be used by fire-fighters in case of fire.

Reaction to fire (fire reaction): The behaviour of a sample when exposed to fire under predetermined conditions in a fire test.

Resistance to heat diode (pyro-insulation): The ability of a building element when exposed to fire on one side to prevent the increase of temperature on the other non-exposed side for a specific time period following a typical fire resistance test.

Unprotected escape route: The first part of an escape route that is surrounded by building elements not subject to special fire resistance requirements that leads to an emergency exit.

Self-closing frame: Frame that is equipped with a mechanism that allows it to close automatically.

Building element: Any building element that is permanently integrated in the building (or construction project or construction). The set of the building elements make up the building or project or construction. The building elements are divided into load bearing and non-load bearing elements, according to whether they are intended to carry the forces exerted on the building, as they are determined by the static analysis of the building.

Emergency exit. An opening into a fire-protected escape route or directly into a safe outdoor area.

Outdoor escape corridor: Outdoor escape corridor with at least one vertical longitudinal side that is open towards an outdoor area. (This surface is considered open even if there is a railing.)

Outdoor stairway: A stairway with at least one side open towards an outdoor area.

Active fire protection: Active fire protection: the fire protection means that are installed in a building and whose purpose is the timely detection and warning in case of fire and/or its prompt containment before it becomes uncontrollable.

Area of risk: High-risk area of the building or space which due to high installed capacity has an increased risk of starting a fire.

Surface flame spread: The spread of flames from the ignition source along the surface of the building element.

Internal finishes: Internal finishes surface construction elements intended for the final formation of internal surfaces of the buildings, like coatings, cladding, paints, joints, insulations, etc.

Load bearing capacity: This is the ability of a load bearing building element to carry a predetermined load for a specific time period following a typical fire resistance test.

Theoretical population: The technical calculation of the number of people inside an area, which is used as the basis of the calculation for taking the right measures and implementing the right means of fire protection, without it being a criterion of the maximum population that may be assembled in that area. It is calculated according to the use of the area and the net surfaces.

Multi-use building: Multi-use building: a building with more than one uses, which are not needed to serve the main use. In multi-use buildings, the individual uses may be either separate or mixed.

One storey building Abuilding consisting of only one above-ground storey, which is also the evacuation storey.

Escape route: The constant and unobstructed route to escape from anywhere inside a building to a safe, usually outdoor area, in case of fire.

Interstitial space: The space gap surrounded by building elements (including the false ceiling) or included inside a building element. Interstitial spaces do not include rooms, cabins, protected shafts, chimneys and various ducts.

Horizontal exit: Exit that provides the possibility to escape from one fire compartment to another on the same storey or to escape from a storey of building to the storey of an adjacent building that belongs to the same proprietor and is almost located at the same height.

Storey: The part of the building that is vertically separated by consecutive floorings, where the minimum distance between floorings is determined in the relevant provisions.

Evacuation storey: The storey of the building where the final exits that lead to a safe outdoor area are situated. For the purposes of this Regulation, every single building is considered to have only one evacuation storey, which is clearly set out in the fire protection analysis, even when due to the ground's morphology, evacuation is possible from more than one levels.

Passive fire protection: The set of measures taken to ensure the timely and secure escape of the public from the building in case of fire, to prevent its collapse and to avoid the fire spreading to other areas or buildings.

Capacity of an escape route: The number of people that may escape in a timely manner, in case of fire, using this route.

Full use: Fulfilment of the minimum number of persons who justify treating the use as separate, as determined by the specific use criteria.

Multi-storey building: A building that consists of more than one storeys above or below ground.

Real distance of an unprotected escape route: The length of the route that a person must cover in order to escape in case of fire, from any point on a storey to the nearest emergency exit.

Fire resistance: The ability of a construction or a building element to resist during a specific time period, which is called fire resistance indicator, to the thermal effects of a fire, without loss of stability, integrity and resistance to the passage of heat.

Fire resistant frame: Self-closing Frame that when tested along with its mounting mechanism and necessary accessories in an integrity and heat resistance test shows a degree of fire resistance. It may have a door restraint mechanism, provided that in the event of fire the shutters are automatically released by order of automatic fire detection and fire-extinguishing systems.

Fire compartment: A part of the building or even a whole building that is hermetically surrounded (in case of fire) by building elements with a predetermined, when relevant, degree of fire resistance. The surface and volume of the fire compartment are calculated in relation to its internal dimensions.

Fire load: The amount of heat that is released by the combustion of all materials that exist in an area. In this case the term "load" refers to energy and is calculated in kJ.

Density of pyrothermal load: It is the pyrothermal load per unit area and is measured in kJ per square meter (kJ/m2).

Fire protected escape route: The part of the escape route (staircase, corridor, hallway, etc.) that is surrounded by fire resistant building elements with a predetermined degree of fire resistance.

Fire seal: A separating element made out of non-combustible materials or materials with a low degree of flammability, that separates an interstitial space or duct or fills joints and gaps between building elements, in order to prevent smoke or flames from passing through them.

Fire extinguishing system: A fire system designed to dynamically stabilise, reduce or stop the spreading of flames, the release of heat or the resulting production of fumes.

Escape plan: A plan on which the necessary escape elements are depicted; it may include the necessary information on evacuation, rescue and first intervention.

Escape plan: The emergency exit on the evacuation storey of the building to which the escape routes end up and which leads directly outside the building to a safe outdoor area connected to a communal or municipal public space.

Areas of main use: Areas intended for the main use of the building and for occupancy by users; examples of these areas in residential buildings are bedrooms, living rooms, kitchens or offices.

Areas for auxiliary use: All of the areas which are not intended for the main use of the building and for occupancy by users, such as circulation areas, corridors, hallways, stairways, sanitary facilities, machine rooms, warehouses, parking areas, buildings intended for animals.

Area for temporary stay -refuge area of people with disabilities: Protected accessible waiting area in which a disabled person may temporarily remain in the event of a fire until he or she is removed from the building. It is usually included in a fire-protected walkway or in the lobby of an elevator and is constructed according to the current specifications.

Area of high risk: Area of a building or of a construction building project, whose contents are highly flammable, are characterised by high speed of surface flame spread and heat release or produce many toxic fumes or entail the risk of explosion.

High tall building: A building whose real height, as determined in relation to its use, is considered crucial and requires additional measures and fire protection means. In general, buildings exceeding 23 metres from the evacuation storey are considered tall buildings.

## Article 4: Building classification according to use

- For the purposes of this Regulation, the eleven uses of buildings that are provided in the Regulation for the construction of buildings shall apply, as described in more detail in Annex A of this document:

| A. | Residence |
| --- | --- |
| B. | Temporary accommodation |
| C. | Public assemblage |
| D. | Education |
| E. | Health & social welfare |
| F. | Penitentiary |
| G. | Commerce |
| H. | Office |
| Ι. | Industry - Small crafts industry |
| J. | Storage |
| K. | Parking areas & petrol stations |

- The use may refer to the whole building or parts thereof.

- In case a building has only one use, then it falls entirely under the scope of the fire protection requirements that apply for this main use.

- When a building has more than one uses, then the following parameters are evaluated in order to define the most adequate means of fire protection (see Annex B):

- The different uses are necessary for the provision of the main use of the building

In case of a building that houses an organisation for the operation of which it is necessary to have more than one uses in the building which serve only the provision of the main use, then the whole building is characterised by its main use and is subject to the fire protection requirements of that predominant use, with the remaining uses being considered “complementary”.

In case the complementary use is fully used, it falls under the provisions that apply to its specific use. In case the complementary use is not separated in a fire resistant way from the predominant use and has no independent escape routes or emergency exits, its theoretical population, which is calculated according to the article relevant to its use, is added to the theoretical population of the predominant use.

Examples of complementary uses are provided in all articles regarding the specific uses of a building in Chapter B of this Regulation. In case of doubt as to the complementarity of a use in relation to the predominant use, the final decision is taken by the responsible Department of the Ministry of Environment and Energy.

- The different uses are independent from one another (separate uses)

In case a multi-use building has several uses that are autonomous, have their own independent escape routes and are separated by fire resistant means, then in terms of fire protection every part of the building is considered separately, is characterised by its own use and is subject to the respective requirements that are set in this Regulation for that specific use.

- The different uses are not independent from one another (mixed uses)

In case a multi-use building has several uses which are provided by common parts of the building (such as corridors and stairways), then the strictest fire protection requirements, where relevant, shall apply for each use, without prejudice to article 7 par. 7.1 of this Chapter in relation to the means of active fire protection.

- One or more of these uses are not used in full, as it is defined

In case of multi-use buildings of category iii (mixed uses) where one or more of these uses are not used by the minimum number of people that would justify considering this use as a separate one, then the fire protection requirements of the other uses apply.

If only one use is used in full, then the fire protection requirements of this use apply and it is considered to be the predominant use, whereas the remaining uses are considered to be complementary. If several uses are used in full, the provisions of the above category iii (mixed uses) apply.

Table 2. Requirements on full use

| Uses not used in full | public assemblage <50 persons |
| --- | --- |
|  | education <6 persons |
|  | temporary accommodation <20 beds |
|  | parking <11 spaces |

- The main and sole use of the building is not used in full

In this case, the applicable fire protection requirements are those described in the specific article on that particular use which refer to the means and measures of another use that is considered to be the most relevant.

- Different sub-categories of the same use (i.e. Ζ1, Ζ2 and Ζ3 for buildings used as Industry - Small crafts industry or Storage, E1, Ε2 και Ε3 for buildings used for Health & social welfare purposes, etc.) are also considered to be different uses and fall under the scope of the aforementioned provisions.

- In buildings or parts of buildings whose use is not included in the categories of paragraph 4.1 of this article, for the application of any regulation on fire protection, the applicable requirements are those of the most relevant category, which is indicated by the responsible Department of the Ministry of Environment and Energy.

- The designation of multipurpose buildings refers exclusively to the existence of more than one use in them regardless of the ownership status of the building.

## Article 5: Escape routes

### Purpose

The main purpose of the escape routes in a building is the safe evacuation of its users in case of fire.

### General

The use of the building and the needs of its users determine the design, the dimensioning and the location of these escape routes.

The escape routes must remain secure and effective for the necessary time frame. In addition, they must be clearly marked and accessible by all users of the building.

It is forbidden to have escape routes in ancillary areas, such as sanitary facilities, storage rooms and electromechanical installations.

The escape routes must not be in the immediate vicinity of hazardous areas of category B (see 6.7).

In case of indoor areas of the main use, i.e. areas accessed through a single horizontal route that passes through another main use area (access area), all of the following six requirements must be met:

a) their theoretical population must not exceed 50 persons;

b) the indoor area must not be a bedroom;

c) the communication between the indoor area and the access area must be direct, without any corridors;

d) the indoor area and the access area must belong to the same owner. (Figure 1)

Figure 2:

Indoor space area with more than one exit

Figure 1:

Indoor area with a single exit

Indoor areas that have more than one exit are exempt from these requirements. (Figure 2)

| χώρος πρόσβασης | Access area |
| --- | --- |
| Εσωτερικός χώρος | Indoor area |
| ΧΩΡΟΣ ΠΡΟΣΒΑΣΗΣ | ACCESS AREA |
| ΧΩΡΟΣ ΜΕ ΕΝΑΛΛΑΚΤΙΚΕΣ ΕΞΟΔΟΥΣ | AREA WITH ALTERNATIVE EXITS |

Escape routes usually consist of three distinct and successive stages: the unprotected escape route, the fire-protected escape route and the horizontal route to the final exit. (Figure 3)

a) The unprotected escape route is the first stage of the route and is the route that leads from anywhere in the building to a safe area, such as: i) a final exit to an outdoor area, ii) an emergency exit on a storey, iii) a horizontal exit.

Usually, the unprotected route is a horizontal route. However, this route may be interrupted by an unprotected staircase or outdoor part, such as an outdoor gallery, an uncovered semi-open space, an accessible flat roof or a balcony.

b) The fire protected escape route is the second stage of the route which begins from the emergency exit (the end of the previous stage of the route) and leads to an exit on the evacuation storey. This whole part is fire protected, i.e. it is surrounded by building elements with the required degree of fire resistance.

Usually, this second stage of the escape route consists of fire protected stairways. Sometimes, it may also include fire protected indoor or outdoor corridors or fire protected hallways.

Escalators or travolators may not be considered as escape routes. It is also forbidden to use lifts as escape routes due to the risk of getting trapped in case of a power failure.

c) The horizontal route towards the final exit is the third and final stage of the escape route. It is the continuation of the fire protected routes from the above or below ground storeys of the building that end up to the evacuation storey and are directed towards the final exit or exits. With this final stage of the route it is possible for the users to escape outside the building, either to an open and safe area of the plot connected to a communal road or directly to an open public space.

If this third stage passes through the building, it must be fire protected and as short and straight as possible.

Public use stairways that continue under the evacuation storey must be interrupted by appropriate separating elements (doors), so as not to cause confusion as to where the final exit is. These separating elements must under no circumstances prevent users from moving towards the final exit or decrease the width of the escape routes.

Final exits must be placed in appropriate locations on the evacuation storey, so that the direction to which the escape route leads outside the building is clear. In addition, they must be protected inside and outside the building against any danger that may be caused by flames or smoke coming from ventilation systems, electromechanical facilities, boiler rooms or other areas of risk.

Parts of the route in this stage that are outside the building must safely lead away from it. In that case, the part of the outside masonry that acts as border to the route must have a degree of fire resistance of at least 30 minutes and any frames must have a degree of fire resistance of at least 15 minutes.

Figure 3: Stages of escape routes

| ABГ: Πρώτο στάδιο όδευσης διαφυγής | ABC: First stage of the escape route |
| --- | --- |
| ГΔ: Δεύτερο στάδιο όδευσης διαφυγής | CD: Second stage of the escape route |
| ΔΕ: Τρίτο στάδιο όδευσης διαφυγής | DE: Third stage of the escape route |
| Υπαίθριος ασφαλής χώρος | Outdoor safe area |

5.3. Design of escape routes

#### Theoretical population

The capacity of the escape route is defined based on the specific use of the building and is calculated for every storey according to its theoretical population.

The values of Table 3 are considered for the calculation of the theoretical population.

In case of separate uses, the values of the Table that correspond to the surface covered by each independent use apply for every separate use.

In case of complementary uses that are not fully used, the calculation of the theoretical population is done according to the requirements of the predominant use for the whole of its surface, including the surface of any complementary areas serving the main use. By way of exception, it is allowed to calculate the theoretical population of complementary areas using the values of Table 3 that relate to their specific use, provided that they are not complementary areas to autonomous residences. In specific buildings containing areas, such as professional kitchens, preparation areas, sanitary facilities, etc., that cannot be included in the uses of article 4 of this Regulation, the person responsible for the analysis may determine their maximum theoretical population based on their real or logically assumed population, which cannot in any case be smaller than the ratio 1 person/30m2.

In case of mixed uses, the theoretical population of each storey is calculated by the sum of the populations of the individual uses, depending on the surface they cover.

Table 3: Calculation of theoretical population by use

| THEORETICAL POPULATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| Category. | Use | Spaces |  | Persons |
| A | Residence |  |  | 1person/18m2 of floor |
| B | Temporary accommodation |  |  | The largest population between the following: S (no of beds, permanent staff), person/18m2 of floor |
| C | Public assemblage areas* | restaurants, cafés, pastry shops, clubs, conference rooms, museums, exhibition areas, locker rooms, etc. |  | 1person/1.40m2 of floor |
|  |  |  |  | For areas with fixed seats: 1 person per seat or for bench seating 1 person per 0.45 m of seat length |
|  |  | auditoriums, concert-lecture-teaching halls, court rooms, theatres, cinemas, sports venues, temples, entertainment areas, bars |  | 1person/0.65m2 of floor |
|  |  |  |  | For areas with fixed seats: 1 person per seat or for bench seating 1 person per 0.45 m of seat length |
|  |  | waiting rooms for means of transportation, standing assemblage areas |  | 1person/0.30m2 of floor |
|  |  | gyms with gym equipment |  | 1person/5m2 of floor |
|  |  | gyms without gym equipment |  | 1person/1.40m2 of floor |
|  |  | sports fields |  | 1person/40m2 of floor |
|  |  | swimming pools |  | 1person/5m2 of floor |
|  |  | areas surrounding swimming pools |  | 1person/3m2 of floor |
|  |  | libraries |  | 1person/5m2 of floor |
|  |  | theatre stages |  | 1person/1.40m2 of floor |
|  |  | airports | public areas | 1person/9m2 of floor (gross surface area) |
|  |  |  | baggage reclaim area | 1person/2m2 of floor (gross surface area) |
|  |  |  | baggage check-in area | 1person/1.4m2 of floor (gross surface area) |
|  |  |  | waiting areas | 1person/1.4m2 of floor (gross surface area) |
|  |  |  |  | For areas with fixed seats: 1 person per seat or for bench seating 1 person per 0.45 m of seat length |
|  |  |  | baggage managing area | 1person/30m2 of floor (gross surface area) |
| D | Education | teaching rooms |  | 1person/2m2 of floor |
|  |  | teaching room with fixed seats |  | The largest population than: number of seats or 1person/2m2 of floor |
|  |  | laboratories |  | The largest population than: workstations or 1person/4.5m2 of floor |
|  |  | other areas (offices, secretary's office, doctor's office, etc.) |  | 1person/2m6 of floor |
| E | Health care | primary health care | diagnosis and treatment without overnight stay | 1person/9m2 of floor |
|  |  | secondary health care | patients rooms | 1person/11m2 of floor |
|  |  |  | other areas (offices, laboratories, ancillary areas, etc.) | 1person/22m2 of floor |
|  | Social care | kindergartens, homes for the elderly |  | 1person/3m2 of floor |
|  |  | ancillary places, warehouses & electromechanical facilities |  | 1person/30m2 of floor |
| F | Penitentiary |  |  | The largest population between the following: T (no of inmates, no of personnel, no of visitors or 1person/11m2 of floor |
| G | Commerce | exhibition & sales area | basement and ground floor | 1person/3m2 of floor |
|  |  |  | stories above ground | 1person/6m2 of floor |
|  |  | Office |  | 1person/10m2 of floor |
|  |  | canteens, restaurants |  | 1person/1.40m2 of floor |
|  |  | corridors of shopping malls |  | 1person/1.40m2 of floor |
|  |  | storage rooms, areas not destined for the public & parking area with up to 10 spaces |  | 1person/30m2 of floor |
| H | Offices | offices <= 50m2 |  | 1person/9m2 of floor |
|  |  | open office spaces > 50m2 |  | 1person/5m2 of floor |
|  |  | waiting areas and receptions |  | 1person/3m2 of floor |
| Ι | Industry - Small crafts industry | Industry - Small crafts industry |  | 1person/10m2 of floor |
|  |  | Industry - Small crafts industry addressed to a specific function |  | Estimated number of users (workers and potential visitors) |
| J | Storage | for commercial reasons (storage rooms, distribution and storage places) |  | 1person/30m2 of floor |
|  |  | simple storage rooms |  | 1person/50m2 of floor |
| K | Parking areas & petrol stations | public parking areas |  | 2 persons / 1 parking space., 1 person / two-wheel vehicle |
|  |  | private parking areas |  | 1 person / 1 parking space., 1 person / two-wheel vehicle |
|  |  | petrol stations - car washes |  | 1 person / 6m2 of floor |
| NOTE: General: the term "floor" refers to the net surface area, excluding fixed furniture or exhibits, with the exception of airports where it refers to the gross surface area. *The surface area of the public assemblage areas includes areas intended only for that particular use. |  |  |  |  |

#### Capacity of escape routes

The capacity of the escape route is defined based on the specific use of the building and is calculated for every storey according to its theoretical population.

The capacity is calculated for horizontal and vertical routes.

For vertical escape routes, the capacity of the above ground storeys of the building (above the evacuation storey) and the underground storeys (underneath the evacuation storey) is calculated separately.

In general, the storey with the highest population defines the necessary capacity of the vertical escape routes. In case of buildings with more than five storeys above the evacuation storey of the building, the total necessary capacity of the vertical above ground escape route is defined by the sum of the population of the two least optimal consecutive storeys.

In case of buildings with more than ten storeys above the evacuation storey of the building, the total necessary capacity of the vertical above ground escape route is defined by the sum of the population of the three at least optimal consecutive storeys.

In case the floor (for buildings up to five (5) above-ground floors) or the two consecutive floors (for buildings above five (5) above-ground floors) or the three consecutive floors (for buildings above ten (10) above-ground floors) with the highest flow, is not the maximum or the upper floors of the building respectively, the provision of the required vertical flow calculated on the basis of their most unfavorable theoretical populations can be applied only for the part of the vertical passage from this most unfavorable population floor or floors to the evacuation floor. Above the storey or storeys that define the necessary vertical capacity, the minimum required vertical capacity is calculated for every storey and the necessary for each case width of the vertical route is selected so that the escape requirements of every storey are met; under no circumstances is it allowed to reduce the width of the route towards the final exit. (Figure 4)

Figure 4: Required exits with width units

| Όροφος | Storey |
| --- | --- |
| Exit 1 | Exit 1 |
| 2 μονάδες πλάτους | 2 width units |

To calculate the capacity, the following are applied:

- In case of uses complemented by complementary uses, the capacity of one storey is the sum of the population of the predominant use and the complementary uses, but it is calculated according to the coefficients in Table 4 that apply to the predominant use.

If the complementary use is used in full, its horizontal capacity in the part that is covered by this particular use is calculated according to the relevant requirements in Table 4. The total capacity for the rest of the storey is the sum of the individual theoretical populations and is calculated as described above, according to the coefficients in Table 4 that apply to the predominant use.

- In case of separate uses, the necessary capacities in Table 4 apply for each separate use, as they are calculated based on their theoretical population.

- In case of mixed uses, the capacity of every storey for the whole of its surface area is calculated using the least optimal coefficients in Table 4 for established uses.

Table 4: Calculation of the capacity of escape routes per width unit (0.60m)

| Cat. | Use |  | Horizontal routes (persons) | Vertical routes (persons) |
| --- | --- | --- | --- | --- |
| A | Residence |  | 100 | 60 |
| B | Temporary accommodation | above ground storeys | 100 | 60 |
|  |  | basements |  | 30 |
| C | Public assemblage areas | above ground storeys | 100 | 60 |
|  |  | basements | 50 | 30 |
| D | Education | above ground storeys | 100 | 60 |
|  |  | basements | 50 | 30 |
| Ε | Health and Social Welfare |  | 50 | 30 |
| F | Penitentiary |  | 100 | 60 |
| G | Commerce | above ground storeys | 100 | 60 |
|  |  | basements | 50 | 30 |
| H | Offices |  | 100 | 60 |
| Ι | Industry - Small crafts industry |  | 100 | 60 |
| J | Storage |  | 100 | 60 |
| K | Parking areas & petrol stations |  | 100 | 60 |

#### Width and height of the escape route

The width of the escape route is the unobstructed width in its narrowest point and up to a height of 2.20 metres.

The width unit of the escape route is set to 0.60 metres.

The required minimum width of any escape route may not be less than 0.70 metres.

The required width of the escape route may not diminish along the route towards the final exit and it is calculated for all stages in relation to the theoretical population and the specific use of the building, expressed in whole width units (0.60 metres). When the result of the calculation is a decimal number, it is rounded to the nearest higher integer by adding half a width unit (0.30 metres).

The unobstructed height of areas traversed by an escape route must be at least 2.20 metres and for stairs, beams or thresholds it may be up to 2.00 metres. Areas where the floor is uneven up to a difference of 0.40 metres and is connected via steps or ramps may be included in the horizontal escape routes.

#### Length of escape routes

The length of the escape route is only examined for its unprotected parts, whereas there is no limit on the length of fire protected parts, which are deemed to be safe.

The length of the examined unprotected escape route is the real distance. Any part of the layout must conform to the minimum distance set from the nearest emergency exit.

The unprotected walking distances on public corridors are measured along the axis line in the middle of the corridor width. In case of unprotected stairs, the measured length on the riser line of the stairs is calculated with an addition of 50%.

The maximum allowed lengths of the above mentioned real distances of escape routes as well as those of any cul-de-sacs (Figure 5) are described in Table 5 according to the use of the building and the ability of the users to escape towards one or more directions - emergency exits.

The number of directions is not equivalent to the number of emergency exits towards fire protected escape routes on the storey. Even if there are more than one emergency exits, it is considered that there is only one escape route when from different parts of the storey the route bypasses the nearest emergency exit in order to access the alternative exit. (Figure 6)

The special provisions may also set, further to the maximum allowed length of unprotected escape routes and cul-de-sacs, additional length requirements for the most remote spot of an area in the building to the nearest exit to a common corridor.

In case the unprotected escape route traverses outdoor areas (outdoor gallery, an uncovered semi-open space, an accessible flat roof or a balcony) to end up again inside the building, the length of this outdoor part of the route must not exceed 1/2 of the total allowed length of an unprotected route and there must not be any cul-de-sacs.

In case the unprotected escape route traverses an outdoor area of the building (outdoor gallery, an uncovered semi-open space, an accessible flat roof or a balcony) to end up directly to the evacuation level, leading to a street or an open area safe from fire or smoke, then to calculate the length of the unprotected distance, the length of the outdoor part is considered as being half the real length, measured from the exit of the building to the outdoor area to the evacuation level.

In existing buildings that fall under the scope of this Regulation (see Table 1) and is not possible to comply with the values in Table 5:

a) the maximum length of a horizontal route, excluding any cul-de-sacs, may be calculated as 2/3 of the real value if all doors of the storey are self-closing and, additionally, there are intermediate fire resistant doors that have vision panels, with a degree of fire resistance of at least 30 min. and are placed at intervals that do not exceed the half (50%) of the values shown in Table 5 (Figure 7);

b) the doors to areas leading to cul-de-sacs, that are longer than the minimum allowed length based on Table 5 must be self-closing;

c) in cul-de-sacs that exceed the maximum allowed length shown in Table 5, there must be intermediate fire resistant doors with vision panels that open towards the direction of the route and have a degree of fire resistance of at least 30 min., so that the parts between these doors meet the requirements concerning the length of the cul-de-sacs that are set in this Regulation.

Figure 5: Dead-end street

| AB: μήκος αδιεξόδου | AB: length of cul-de-sac |
| --- | --- |
| Έξοδος | Exit |

Figure 6: Escape directions

| χώρος 1 | area 1 |
| --- | --- |
| ΣΗΜΕΙΩΣΗ Από τον χώρο 1 υπάρχει μία μόνο κατεύθυνση διαφυγής διότι για να χρησιμοποιηθεί η έξοδος Δ' ο ένοικος προσπερνά την πλησιέστερη έξοδο Ζ. Από τον χώρο 2 υπάρχουν δύο κατευθύνεις διαφυγής, διότι από το σημείο Γ' του κοινόχρηστου διαδρόμου ο ένοικος μπορεί να επιλέξει δύο διαφορετικές πορείες, μία προς την έξοδο Ζ και μία προς την έξοδο Δ' | NOTE There is only one escape direction from area 1 because in order to use exit D the tenant bypasses the nearest exit F. There are two escape directions from area 2 because from point C of the common corridor the tenant may choose between two different routes, one towards exit F and one towards exit D. |
| Γ | C |
| Δ | D |
| Ε | E |
| A | A |

Table 5: Length limits of real unprotected route by category of use (in metres)

| USE CATEGORY OF THE BUILDING |  | ONE DIRECTION | MORE DIRECTIONS | DEAD-END STREETS |
| --- | --- | --- | --- | --- |
| A | Residence |  |  |  |
|  | Detached houses | 25 | 35 | 12 |
|  | Apartment blocks | 18 | 35 | 9 |
| B | Temporary accommodation | 18 | 35 | 9 |
| C | Public assemblage areas |  |  |  |
|  | With fixed seats | 15 | 32 | 9 |
|  | Without fixed seats | 18 | 45 | 9 |
| D | Education | 18 | 35 | 9 |
| E | Health & social welfare | 15 | 35 | 9 |
| F | Penitentiary | 15 | 35 | 9 |
| G | Commerce | 18 | 45 | 9 |
| H | Offices | 18 | 45 | 9 |
| Ι | Industry - Small crafts industry |  |  |  |
|  | Low and medium risk (Ζ1, Ζ2) | 251 | 451 | 15 |
|  | High risk (F3) | 122 | 252 | 0 |
| J | Storage |  |  |  |
|  | Low and medium risk (Ζ1, Ζ2) | 251 | 451 | 15 |
|  | High risk (F3) | 122 | 252 | 0 |
| K | Parking areas & petrol stations | 15 | 45 | 9 |

1: In case there is an automatic water based fire extinguishing system (water sprinkler), the length limit is doubled.

2: In case there is an automatic water based fire extinguishing system (water sprinkler), the length limit is multiplied by 1.5.

Figure 7: Intermediate fire resistant doors in corridors of existing buildings when the maximum allowed length of unprotected route is not respected

#### Number, location and doors of emergency exits

In general, in every storey with a population of more than 50 persons, it is necessary to have at least two alternative emergency exits.

The emergency exits from any point of the area must be placed in locations clearly visible by the users.

If there are two (2) or more emergency exits, the distance between their nearest ending points must be at least 1/2 of the maximum diagonal dimension (D) of the area or building they serve. (Figures 8 and 9)

If there are three (3) or more emergency exits, the location of at least two (2) of them must fulfil the above mentioned criteria.

The doors of the emergency exits must open towards the direction of the escape route, when the estimated population of the area or part of the building is more than 50 persons or when it is considered as a high risk area or part of the building.

The unobstructed opening of the doors of the emergency exits is at least 0.90 metres.

The emergency exits to which the unprotected escape stage end up usually lead to an equivalent number of fire protected stairways. However, it is possible that more than one emergency exits lead to the same fire protected escape route, if:

a) the vertical route covers the total required capacity based on the population of that storey;

b) the maximum length of unprotected routes that is defined for that particular use of the area is met starting from any point of the layout of that storey.

In any case, if the vertical capacity exceeds three width units (1.80 m), there must be an additional stairway - vertical escape route.

When designing the building, care must be taken to allocate the population at the stairways as evenly as possible, and the maximum allowed derogation when comparing the width dimensions of these stairways must not exceed 30%.

In buildings where the highest floor level for a main use is up to 23 m, and the emergency exits are connected to a fire protected corridor with a degree of 60 minutes, instead of the diagonal it is possible to use the smallest length connecting the exits, measured at the middle of the active width of the corridor. (Figure 10)

Figure 10

Figure 8

Figure 9

| --- ενεργό μήκоς πυροπροστατευμένоυ διαδρομου Για τις εξόδους A και Γ πρέρει: AB+BΓ>D/2 | --- active length of a fire protected corridor For exits A and C: AB+BC>D/2 |
| --- | --- |
| Διαγώνιος D | Diagonal D |

In any case, the width of the exits on the evacuation floor to which the vertical fire protected escape routes end up must suffice for the respective vertical capacities.

### Horizontal exits may replace up to half of the necessary emergency exits, if their level isn't higher than 23 metres from the level of the evacuation floor.

In case of horizontal exits, further to the other requirements, in order to ensure the gradual horizontal evacuation of the storey's population:

a) the surface area of the fire compartments on both sides of the horizontal exit, if the horizontal exit is two-directional, must be sufficient for the sum of the theoretical populations of both fire compartments, with a minimum coefficient of 0.3m2/person. (Figure 11) In case of a one-direction horizontal exit, this requirement must be met for the fire compartment towards which leads the horizontal exit;

b) the remaining fire exits must lead to fire protected escape routes, where it is not allowed to use controlled access doors which obstruct the route;

c) the degree of fire resistance of the separating wall bearing the horizontal exit must be at least 120 minutes without the possibility of reduction due to the presence of an automated water based fire extinguishing system (water sprinklers);

d) the partition wall of the horizontal exit can not be replaced by fireproof shutters or similar structural elements, while the exit doors will be EI120 and smoke-proof, performance of class Sm according to EN13501-2.

e) no ducts are allowed through the wall that bears the horizontal exit.

### 0.3>(Surface DV1/theor.pop. P1 + theor. pop. Π2)

### 0.3>(Surface P2/theor. pop. P1 + theor. pop. Π2)

Figure 11: Horizontal exit

In specific buildings, any bridges, exterior balconies or any other exit that leads from the building to another building of the same use and same proprietor may replace other necessary exits up to 50%, if their level isn't above 23 metres from the level of the evacuation storey and provided that no controlled access doors are used in the rest of the obligatory escape routes.

#### Final exit

The necessary width of the final exit on the evacuation storey must be adequate for the horizontal capacity that is required for the population's evacuation, which in case of fire will be gathered in that storey. However, due to the gradual evacuation of the buildings from the storeys above and below ground, the necessary width of the final exit is calculated as the sum of:

a) the width of the necessary vertical capacity of higher storeys,

b) the width of the necessary vertical capacity of lower storeys,

c) the width of the horizontal capacity of the evacuation storey,

as obtained before rounding them to whole units of width. Before being rounded to whole width units, afterwards, only the width of the final exit is rounded.

Where the sum of α+b+c is greater than two units of width, the required vertical flow rate (a) from above-ground floors plus 25 % shall be taken for the calculation of the width of the final output.

In case where due to the building's design it is necessary that the above and below ground storeys are evacuated through fire protected escape routes leading directly to a safe area outside the building that has independent final exits that do not communicate with the rest of the building and ensure the necessary width of vertical capacities, their capacities are not added to the calculation of the minimum width of the final exits on the evacuation floor of the third escape stage (horizontal route towards the final exit). In case however where under the aforementioned conditions there is the possibility for communication of the area where the fire protected vertical escape routes end up in the evacuation storey with other areas in that storey that have own exits, then to calculate the width of the final exits in the evacuation storey, 50% of the vertical capacities of the above and below ground storeys of the building is also taken under consideration.

In any case, the width of the exits on the evacuation floor to which the vertical fire protected escape routes end up must suffice for the respective vertical capacities.

If there are steps after the final exit, there must also be a ramp of sufficient width, to allow for the removal of people with disabilities.

It is forbidden to place areas of risk under or next to final exits.

#### Doors of the escape routes

#### General

In every door opening at the first stage of the escape route (unprotected route), there must be at least one door panel that is no less than 0.7 metres wide. By way of exception, doors to ancillary areas (warehouses, sanitary facilities, etc.) may be at least 0.60 metres wide (unobstructed width). No door panel connected to an escape route may be more than 1.20 metres wide.

The floor on both sides of every door must be levelled and on the same height. By way of exception, when the door leads outdoors or to an open area (outdoor gallery, an uncovered semi-open space, a flat roof) or towards the final exit, the level of the floor may on the outer side of the door be up to 0.20 m lower than the floor level on the inside.

The fire resistance requirements of the doors of the escape routes are defined in Table 6 of this chapter.

#### Door rotation direction

Any door that is used as an emergency exit, must in general open fully to the direction of the exit. (Figure 12)

Figure 12: Full door opening

An exception is provided for doors that serve areas that are not considered of risk or of high risk with a total population of up to 50 persons. These doors may also open towards the opposite direction of the escape route or they may be sliding doors.

Any door that leads directly to a staircase must not obstruct any steps or landings nor reduce the width of a stairway or landing, ensuring at least one width unit of escape route. (Figure 13)

Figure 13: Door opening on a stairway landing

| Σωστό | Correct |
| --- | --- |
| Λάθος | Incorrect |

##### Automatic mechanical doors with movement sensors that exist on the escape routes or used as emergency exits are allowed only if they provide the necessary unobstructed width when fully open and remain open in case of a power failure.

#### Door equipment

Every door must be equipped with a proper mechanism, so that it opens directly towards the direction of the escape route in an obvious and easy way.

Any fire resistant door that is intended to remain closed in case of fire (i.e. a door to the stairway enclosure, a door to a fire compartment, etc.) must be self-closing.

If it is equipped with a retention mechanism to keep it open, it is imperative that it can be deactivated in the following ways:

a. manually via a suitable device (button) on site;

b. from the building's control panel;

c. in case of a power failure;

d. in case the fire detection system is activated;

e. in case the automatic fire extinguishing system is activated.

Bolts or other such means or security systems (such as keys, magnetic cards, keyboards) are not allowed.

##### Route retention-control doors

##### Automatic mechanical doors with movement sensors that are used as emergency exits are only allowed if they provide the necessary width when fully open and remain open in case of a power failure.

Security doors with special time delay mechanisms are allowed only as secondary emergency exits and must be automatically released in case of a power failure or in case the automatic fire detection system or the automatic fire extinguishing system is activated, if applicable, as well as manually via a release button. When calculating the width units of the escape route, 50% of their width is counted.

Doors revolving around a vertical main axis when considered as secondary alternative routes they are used in the calculation of the width units of the escape route counting the half (50%) of their width.

Revolving obstacles or assemblies to control incoming people (for instance in sports fields) are not allowed as parts of escape routes.

#### Railings

Stairways, landings, balconies and ramps that are parts of escape routes must have railings. The handrails must be continuous along the entire length of the stair or ramp branch and continue on the wide steps.

The necessary parapets and/or railings must be at least 1 meter high, measured from the level of the steps of the stairway.

In every staircase used as an escape route, where the width of the stairs must be higher than 1.80 metres, there must be intermediate railings, so that the maximum width of every part of the stair is 1.80 metres and the minimum 0.90 metres.

### 5.4. Artificial lighting and emergency lighting of the escape routes

#### Artificial lighting

The artificial lighting must be powered by constant power sources. It is forbidden to use lights that are battery powered or movable elements for the regular lighting of escape routes.

It is forbidden to use phosphorescent or light reflecting elements as substitutes to the necessary electrical lights.

#### Emergency lighting

The emergency lighting is designed and installed according to the ELOT (Greek Standards Organisation) EN 1838 standard: “Illuminating applications – Security lights”, as in force.

Emergency lighting must be installed on all escape routes and emergency exits.

Emergency lights must provide 50% of their luminosity in 5 seconds and reach full luminosity in 60 seconds, according to the ELOT EN 1838 standard.

Emergency and signs lights must provide the designated light for at least 1 hour, in case of failure of normal lighting.

In escape routes up to 2 m wide, the luminosity of the floor along the main axis of the escape route shall not be less than 1lx and for the zone next to the escape route, whose width is at least half of that of the escape route, the luminosity of the floor shall not be less than 0.5lx, according to the ELOT EN 1838 standard, without prejudice to any stricter requirements that are defined in the special provisions of chapter B of this Regulation for the different uses of the buildings.

It is necessary to have emergency and signs lighting installed, irrespective of whether there is an auxiliary power source.

### Escape route signs

Escape signs, as well as signs concerning the fire fighting equipment and its inherent features must be placed according to the ELOT EN ISO 7010 standard: "Graphic symbols – Safety colours and safety signs – Registered safety signs", in its current version, upon consideration of the provisions of the PD (Presidential Decree) 105/1995 (A’ 67) "Minimum requirements for the provision of safety and/or health signs at work in compliance with Directive 92/58/EEC".

Escape routes, emergency exits and fire fighting equipment must have safety signs.

### Escape plans.

The escape diagrams and symbols with the corresponding plates shall comply with ISO 23601: “Safety Identification — Escape and evacuation plan signs”, as applicable.

In general, fire escape diagrams must be provided in buildings whose main use covers three (3) or more storeys and which have a theoretical population of more than two hundred (200) persons, as well as according to the provisions of chapter B of this Regulation on the different uses of the buildings.

### Fire-fighters staircases and lifts

In high tall buildings, as defined in the Table 6, in buildings with large underground areas or with a very big difference from the ground level, as well as wherever it is necessary due of the specific use of the building, there must be special stairways or lifts that allow the access to fire-fighters. (Table 6)

The stairways of the building can also be considered as fire-fighters stairways, if they meet the relevant requirements.

### Fire-fighters staircase

This is a permanent fire protected indoor or outdoor staircase, that is specifically constructed to allow the access of fire-fighters. In general, fire-fighters staircases are obligatory: It is generally imposed on:

a) in buildings taller than 25 metres with a total population of over 500 persons,

b) underground spaces with a depth greater than 10 m.

c) in buildings with two or more basements, when each basement has a surface area of more than 900 m2,

as well as wherever it is required by the specific provisions of this Regulation.

The minimum width of the fire-fighters stairway is 0.90 metres. This minimum width of the 0.90 m. must be ensured in addition to the total width of the stairways that is required for the escape of the tenants. The fire-fighters staircase can also be used as an escape route for the tenants.

### Fire-fighters lifts

In buildings taller than 28 metres, and wherever it is required by the special provisions, there must be a lift to be used by fire-fighters in case of fire.

The lift must meet the requirements of the EN 81 standard, Part 72: Fire-fighters lifts.

According to the standard, the following characteristics are requirements that must be met by the design of the building in order for a lift to be considered as a fire-fighters lift:

- The entrance to the fire-fighters lift in every storey shall be through a fire protected hallway.

- The fire-fighters lifts are not escape routes, like stairways.

- The provision of movement and lighting power must be ensured both from a main and an auxiliary power source which must be situated inside the fire protected area.

- The fire-fighters lift must serve all the storeys in the building.

- The aforementioned EN 81 standard lays down the minimum dimensions and the minimum nominal load of the lift cabin.

The fire-fighters lift may be used as a passenger lift under normal operating conditions of the building. It is forbidden to use the lift to carry waste or other objects, in order to rule out the possibility of obstructing its entrance on any storey.

Table 6 below presents, in addition to the above general requirements for the construction of fire-fighters stairways and lifts which apply to all building uses, further requirements on their installation by category of use, in order to be used only by fire fighters.

Figure 14: Avελκυστήρας και κλιμασκοστάσιο πυροσβεστών με εξωτερική πρόσβαση

| Avελκυστήρας και κλιμασκοστάσιο πυροσβεστών με εξωτερική πρόσβαση | Fire-fighters lift and stairway with outdoor access |
| --- | --- |
| Πρόσβαση στο κλιμακοστάσιο πυροσβεστών μέσω διαδρόμου | Access to the fire-fighters staircase through a corridor |

Table 6: Construction requirements of fire-fighters stairway and lift

| GENERAL REQUIREMENTS |  |  |
| --- | --- | --- |
| Buildings, irrespective of use | Fire-fighters lift | Staircase of firefighters |
|  | Buildings of high Buildings taller than 28 metres | Buildings taller than 25 metres with a population of more than 500 persons |
|  |  | Underground spaces whose floor lies >10 metres below ground |
|  |  | Buildings with two or more basements, when each basement has a surface area of >900 m2 |
| ADDITIONAL REQUIREMENTS |  |  |
| Category of use | Fire-fighters lift | Staircase of firefighters |
| Temporary accommodation | >6 above ground storeys | General requirements |
| Education * | Height >15 metres | Height >15 metres |
| Offices | Height >15 metres and storey surface >500 m2 | General requirements |
| Commerce | Height >15 metres and storey surface >500 m2 | General requirements |
| Public assemblage areas* | Floor level above 15 m. | Floor level above 15 m. |
| Health & social welfare** | Floor level higher than 12 metres | Floor level higher than 20 metres |

Note: Reported heights shall be measured from the level of the evacuation deck

* Only one of these requirements applies.

** Real distance of the horizontal unprotected route to the staircase or the lift less than 45 metres. Unobstructed width of the lift's cabin of at least 1.70 metres and unobstructed depth of at least 2.40m.

## Article 6: Structural fire protection

- General

The purpose of the provisions of this article is to reduce the risk of collapse of the whole building or part of it due to a fire, the risk of the fire spreading inside the building as well as the risk of the fire spreading to nearby buildings and other constructions. In particular, the following are defined:

- the minimum degree of fire resistance of the load bearing building elements, the fire protected escape routes and of the fire compartments of the building, according to their use and size,

- the maximum allowed surface and volume, as defined in the special provisions on the different uses in chapter B, of the fire resistant separation of buildings according to their use and any risk that may be connected to their contents (fire compartmenting),

- high risk areas (areas of risk) that must consist of a separate fire compartment,

- the fire reaction requirements on indoor finishings of areas, according to their use,

- measures on the protection of indoor and outdoor vertical escape routes,

- the fire reaction and fire resistance requirements on external building elements of the sides of the buildings, in relation to adjacent buildings.

The fire protection specifications of construction products and building elements are divided in two basic categories, according to their respective specifications:

1. The behaviour in relation toν ”reaction to fire” (reaction to fire) applies to construction products, such as interior finishings, which are expected to be directly exposed to the fire during its early phases. In that case, the basic fire protection aim is to contain the spread of the fire and smoke, as well as to prevent or delay flashover. Annex D contains additional information on the way that construction products are classified in the Euroclass system and on fire reaction tests.

2. The behaviour in relation to “fire resistance” (fire resistance) applies to load bearing and non-load bearing building elements, as well as separating elements of fire compartments, which are expected to be exposed to fire during the phase of fully developed fire that comes after flashover. In that case, the main fire protection aim is to contain the fire in the area (or building) where it started, as well as to prevent structural failures. The classification system set out in the Annex to Commission Decision 2000/367/EC of 3of May 2000 implementing Council Directive 89/106/EEC as regards the classification of construction products and parts thereof according to resistance to fire performance shall apply for classes of fire resistance performance. Additional information on ways to determine the degree of fire resistance of building elements and on fire resistance tests may be found in Annex C.

- Requirements on the degree of fire resistance

The fire resistance requirements apply to load bearing elements of the building in order to ensure that it won't collapse, the fire protected escape routes for the secure evacuation of the building's users and the envelopes of the fire compartments of the building, in order to contain the fire inside the building (see Annex C).

The minimum degree of fire resistance for each building use and in relation to its height is presented in Table 7.

Table 7: Requirements on the degree of fire resistance per building use

| MINIMUM ALLOWED DEGREES OF FIRE RESISTANCE |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Category | Use |  | Subcategory |  | Minimum degree of fire resistance (in minutes) |  |  |  |  |  |
|  |  |  |  |  | Underground storeys |  | Above ground storeys |  |  |  |
|  |  |  |  |  | height >10 metres* | height of ≤ 10 m * | up to 2 storeys and ≤5 metres (highest floor level) | between 3 and 6 storeys and ≤ 15 metres* | between 7 and 10 storeys and ≤ 27 metres* | >27 metres |
| A | Residence |  |  |  | 90 | 60 | 30 | 60 | 90 | 120 |
| B | Temporary accommodation |  |  |  | 90 | 60 | 30 | 60 | 90 | 120 |
| C | Public assemblage areas |  |  |  | 120 | 90 | 60 | 90 | 120 | 180 |
| D | Education |  |  |  | 90 | 60 | 30 | 60 | 90 | 120 |
| E | Health & social welfare |  |  |  | 120 | 90 | 60 | 90 | 120 | 180 |
| F | Penitentiary |  |  |  | 120 | 90 | 60 | 90 | 120 | 180 |
| G | Commerce |  |  |  | 120 | 90 | 60 | 90 | 120 | 180 |
| H | Offices |  |  |  | 90 | 60 | 30 | 60 | 90 | 120 |
| Ι | Industry - Small crafts industry** |  | I1 |  | 120 | 90 | 60 | 90 | 120 |  |
|  |  |  | I2 |  | 180 | 120 | 90 | 120 | 180 |  |
|  |  |  | I3 |  | 240 | 180 | 90 | 180 | 240 |  |
| J | Storage** |  | I1 |  | 120 | 90 | 90 | 120 | 180 |  |
|  |  |  | I2 |  | 240 | 180 | 120 | 180 | 240 |  |
|  |  |  | I3 |  | 240 |  | 180 | 240 |  |  |
| K | Parking areas & petrol stations** |  | L1, L2open |  | - | - | 30 | 60 | 90 |  |
|  |  |  | L1, L2, L3, closed and L4 |  | 120 | 90 | 60 | 90 | 120 | 180 |
| * The level of the floor of the lowest storey for underground storeys or the highest storey for above ground storeys that are above the evacuation storey. ** The Ζ1, Ζ2 and Ζ3 categories are analysed in articles 9 & 10 of Chapter B. *** The categorization L1, L2, L3 and L4 are analysed in article 11 of Chapter B. |  |  |  |  |  |  |  |  |  |  |

In case there is an automatic water based fire extinguishing system (sprinkler) in the fire compartment, the degree of fire resistance may be reduced by 60 minutes, but in no case can it be less than 60 minutes.

The degree of fire resistance of a building element is defined according to the fire resistance tests as described in the EN 13501 standard and concerns many criteria/performance, that are presented in Annex C. However, the term fire resistance usually refers to meeting the following three criteria: of load bearing capacity (R), integrity (Ε) and heat resistance (Ι).

In some cases it is not necessary for building elements, depending on their location and the building's use, size and estimated risk, to meet all three criteria/performance, but may instead meet one or more of these or, additionally, one or several of the remaining criteria.

The necessary fire resistance criteria/performance that must be met by building elements are defined in Table 8.

Table 8: Minimum required performance criteria for fire resistance indicators of structural elements

| Building elements | Minimum performance criteria |
| --- | --- |
| Load bearing masonry (indoor and outdoor) | REI |
| Outdoor non load bearing masonry | ΕΙ |
| Load-bearing vertical elements (support stands, walls, frame systems, etc.) | R |
| Fire resistant doors, windows and window panes | ΕΙ |
| Exterior non-load-bearing masonry, fire-retardant walls and fire department walls | ΕΙ |
| Separating building elements of storeys – fire seals (plates & beams) | REI |
| Walls of stairways | ΕΙ |
| Load bearing elements of stairways | R |
| Self supporting roof coverings (panels, etc.) | REI |

- Load bearing building elements

The load bearing structure of the building must, in case of fire, be able to bear the loads for which it is designated, for a time frame defined by the degree of fire resistance for each building use. This requirement applies to the whole of the load bearing structure as well as on its individual elements.

To design the load bearing building elements against fire, the designers may use the Eurocodes (ELOT EN 1990 -1999 norms), as they are applied in Greece, in conjunction with the respective National Appendixes (ELOT EN 199X/NA), taking under consideration the minimum required degrees of fire resistance provided in this Regulation (Table 7), as well as other relevant requirements. The design shall be according to calculation methods that are reported in the respective Eurocodes or based on the relevant Eurocode tables, if the criteria on use that are defined in the respective Eurocodes are met. In exceptional cases, if it is required and the relevant requirements are met, advanced methods may be used as well as calculation simulations and general principles of fire engineering.

To determine the required degree of fire resistance for each building element, irrespective of the type of its material, it is necessary to have the certificates required by the relevant standards.

In special cases or if the required certificates are not available, the degree of fire resistance or other fire resistance qualities shall be defined based on relevant standard tests which shall be performed by laboratories certified to perform such tests.

The above also applies to non-load-bearing structural elements and materials.

Excluded from the fire resistance requirements for the load bearing structure, are autonomous and functionally independent ancillary one-storey buildings, that meet all of the following requirements:

- there is no basement and no provision for future storeys

- their gross height is up to 4.50 metres;

- their gross surface is up to 100 m2.

- there are no spaces of risk, nor high risk areas.

These buildings remain bound by the remaining requirements on structural fire protection.

- Fire protected escape routes

The building elements of the envelopes of fire protected escape routes, i.e. walls, floors, ceilings and frames, as well as any fire protected hallways must have the minimum degree of fire resistance as defined for each building category, according to the building's use. (Table 7)

The fire resistant frames of fire protected routes must, in general, be self-closing and their degree of fire resistance may be 30 minutes less than what is required for the fire compartment, but it may not be less than 30 minutes.

- Fire compartmenting

The separation of a building in fire compartments aims at containing the fire within the area where it started and preventing its horizontal and/or vertical spread to the rest of the building. For any building category, a maximum surface limit (Table 9) is defined and, for some specific uses, a maximum volume as well, beyond which the building must be separated in fire compartments. (Figure 15)

Figure 15: Fire compartmenting

It is obligatory to consider as separate fire compartments all areas of risk, with the same degree of fire resistance that is required for the rest of the building and, in any case, not less that 60 minutes.

In basements of buildings extending to a depth of more than 10 m below ground level, each particular basement part area must be a separate fire compartment and must be fireproofly separated from the other basements.

In all the other cases of basements areas of buildings that do not extend to a depth greater than 10 m., a fireproof separation between the basements storey areas is not required, except between the roof of the first basement and the superstructure, where a fireproof separation should exist (Figure 16). By way of exception, in buildings of all uses except categories E only for subcategory E3, G, H only for high-risk establishments, I for subcategory G3, K and L only, non-fire resistant separation of the first basement from the superstructure is permitted, provided that it is functionally linked to its use and the total area of the fire compartment created does not exceed the maximum authorised surface area of a basement fire compartment for each use, as set out in Table 9 of this Article (Figure 16c).

Figure 16: Fire separation of basements

(b)

(a)

(b)

(a)

| Ρηχά υπόγεια βάθους<10 μ που δεν περιλαμβάνουν κύρια χρήση κατοικίας | Shallow basements of less than 10 metres deep that are not used as residence |
| --- | --- |
| πυροδιαχωρισμός | fire separation |
| ΑΝΩΔΟΜΗ | SUPERSTRUCTURE |
| ΥΠΟΓΕΙΟ | BASEMENT |
| Βαθιά υπόγεια>10μ. | Deep basements >10 metres |
| πυροδιαχωρισμός | fire separation |
| Πυροδιαμέρισμα | Fire compartment: |
| 1ο υπόγειο | 1o basement |

The building elements of the envelope of a fire compartment, i.e. walls, floors, ceilings and frames, must have the minimum degree of fire resistance as defined for each building category, according to the building's use. (Table 7)

All frames (except for external ones) on fire compartment walls must be fire resistant and have the same degree of fire resistance that is required for the respective wall, reduced by 30 minutes, but in any case not less than 30 minutes.

In certain uses of buildings, fire-resistant rolls or fire-curtains of equivalent integrity and thermal insulating capacity may be used in place of fixed building elements, in accordance with the case-by-case requirements of the specific provisions of Chapter B. In any case fire-resistant rolls may not replace walls of underground fire compartments and dangerous spaces.

The machine rooms of lifts are preferably installed (especially in multi-storey buildings) at the top of shafts and must be enclosed in building elements that have a degree of fire resistance of at least 60 minutes.

In multi-use buildings with mixed uses, the least optimal degree of fire resistance is assumed, as shown in Table 7.

In buildings with complementary uses that are not used in full, the degree of fire resistance of the predominant use is t assumed, according to Table 7. In case the complementary uses are used in full, for each use the degree of fire resistance that is relevant to it is assumed, whereas the load bearing building elements and the fire protected escape routes meet the degree of fire resistance of the least optimal use, given that the degree can under no circumstances be reduced near the evacuation storey of the building.

In multi-use buildings with separate uses:

- the building elements of the envelope of every fire separated use meet the requirements of Table 7 for each use,

- the load bearing building elements and the fire protected escape routes meet the degree of fire resistance of the least optimal use, given that the degree can under no circumstances be reduced near the evacuation storey of the building,

- the building elements used in common separating elements (vertical and horizontal) must meet the degree of fire resistance of Table 10 resulting from the combination of separate uses.

In any case, every autonomous residence must be separated in a fire resistant way from adjacent properties or uses.

Additionally, in all buildings excluding those of class Ε1 and Ε3 used for Health and social welfare purposes, as well as those in category Storage, in case there are covered patios, it is allowed to compartmentalise areas adjacent to the patio using, instead of fixed building elements, fire resistance roller shutters or fire curtains of an equivalent integrity and heat insulation capacity that are connected to the fire detection system and close in less than 1 minute. These elements must not affect the design of escape routes and must, additionally to have an auxiliary power sources.

Table 9: Maximum surface area of fire compartments

| MAXIMUM SURFACE AREA OF FIRE COMPARTMENTS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Category | Use |  | Maximum surface area of fire compartments (in m2) |  |  |  |
|  |  |  | Basements | One storey building | Multi-storey building | Addition due to the presence of an automatic water based fire extinguishing system (water sprinkler) |
| A | Residence |  | 500 | no requirement | 1000 | 2 |
| B | Temporary accommodation |  | 500 | 2000 | 1000 | 2 |
| C | Public assemblage areas | General | 500 | 4000 | 2000 | 2 |
|  |  | Airports | 500 | 4000 |  |  |
|  |  | Playgrounds sport areas and spectators areas in Sports facilities | 500 | 10000 |  |  |
| D | Education |  | 500 | 2000 | 1000 | 2 |
| E | Health care |  | 500 | 2000 | 1000 | 2 |
|  | Social welfare |  | 500 | 2000 | 1000 | 2 |
| F | Penitentiary |  | 500 | 1500 | 750 | 2 |
| G | Commerce | General | 500 | 2000 | 1000 | 2 |
|  |  | Shopping malls | 500 | 4000 | 2000 | 2 |
| H | Offices |  | 500 | 2000 | 1000 | 2 |
| Ι | Industry - Small crafts industry | Ζ1 | 1000 | 10000 | 3000 | 2 |
|  |  | Ζ2 | 1000 | 5000 | 2000 | 2 |
|  |  | Ζ3 | 1000 | 4000 | 1500 | 2 |
| J | Storage | Ζ1 | 1000 | 5000 | 2000 | 2 |
|  |  | Ζ2 | 750 | 4000 | 1500 | 2 |
|  |  | Ζ3 | 500 | 3000 | 1000 | 2 |
| K | Parking areas - Car wash |  | 500 | 2000 | 1000 | 2 |

Table 10: Required degree of fire resistance between different uses

| Minimum degrees of fire resistance (in minutes) of separating building elements in case of separate uses |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| USE | RESIDENCE | TEMPORARY OCCUPANCY | PUBLIC ASSEMBLAGE AREAS | EDUCATION | HEALTH AND SOCIAL WELFARE | PENITENTIARY | COMMERCE | OFFICE | INDUSTRY (Ζ1-Ζ2) | INDUSTRY (I3) | STORAGE (Ζ1-Ζ2) | STORAGE (Z3) | PARKING |  |  |
| RESIDENCE | - | 60 | 120 | 90 | 120 | 120 | 120 | 90 | 120 | 180 | 120 | 180 | 120 |  |  |
| TEMPORARY OCCUPANCY |  | - | 120 | 120 | 120 | 120 | 120 | 90 | 120 | 180 | 120 | 180 | 120 |  |  |
| PUBLIC ASSEMBLAGE AREAS |  |  | - | 120 | 120 | 120 | 120 | 60 | 120 | 180 | 120 | 180 | 120 |  |  |
| EDUCATION |  |  |  | - | 120 | 120 | 120 | 90 | 180 | 180 | 180 | 180 | 120 |  |  |
| HEALTH AND SOCIAL WELFARE |  |  |  |  | - | 120 | 120 | 60 | 120 | 120 | 120 | 120 | 120 |  |  |
| PENITENTIARY |  |  |  |  |  | - | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  |  |
| COMMERCE |  |  |  |  |  |  | - | 90 | 120 | 180 | 120 | 180 | 120 |  |  |
| OFFICES |  |  |  |  |  |  |  | - | 120 | 180 | 120 | 180 | 120 |  |  |
| INDUSTRY (Ζ1-Ζ2) |  |  |  |  |  |  |  |  | - | 90 | 60 | 90 | 90 |  |  |
| INDUSTRY (Z3) |  |  |  |  |  |  |  |  |  | - | 90 | 60 | 90 |  |  |
| STORAGE (Ζ1-Ζ2) |  |  |  |  |  |  |  |  |  |  | - | 90 | 90 |  |  |
| STORAGE (Z3) |  |  |  |  |  |  |  |  |  |  |  | - | 90 |  |  |
| PARKING |  |  |  |  |  |  |  |  |  |  |  |  | - |  |  |
| 1. In case there is an automatic water sprinkler system in the whole building, the above mentioned values are decreased by 60 minutes, but remain above 60 minutes at the lowest. 2. The degrees of Table 7 apply in case for some uses the values are higher than the ones defined above. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

- Fire spread within the building

- General requirements

To prevent the fire spreading from one fire compartment to another, the walls of the fire compartments must extend above the ceiling through gaps in the ceiling - roof or through the interstitial spaces and over the roof cover by at least 0.50 metres. (Figure 17)

Figure 17:

In case of a flat roof for which it is impossible to have such an extension, there must be provisions from both sides of the wall, in a distance of at least 1.50 metres, for a proper coating protection using non-combustible materials.

| επικάλυψη στέγης ή οροφής | roof or ceiling coating |
| --- | --- |
| τοίχος πυροδιαμερίσματος | fire compartment wall |
| επικάλυψη δώματος | flat roof coating |
| διάκενο | interstitial space |
| τοίχος πυροδίαμερίσματος | fire compartment wall |

Floor openings that are necessarily created between floors due to the presence of stairs, ramps, lifts, skylights, air ducts, etc., must be surrounded by vertical fire protected shafts, with the relevant fire resistant frames. Openings that are within the limits of the same fire compartment are excluded from this requirement, irrespective of whether the compartment covers two or more storeys.

Piping and cabling is allowed to penetrate the envelope of the fire compartment or the fire protected shafts, if their internal diameter is less than 40 mm. If constructed using non-combustible materials, with a melting point of over 800οC, they can penetrate even if their internal diameter is up to 160 mm. Ducts made out of several materials (lead, PVC, aluminium, etc.) with an internal diameter of up to 160 mm may penetrate building elements of fire compartments, if they are covered, to a length of at least one metre on both sides, with non-combustible materials. The gap between the duct and the building element must be as small as possible and be filled by an adequate fire seal (Figure 18).

Chimneys or smoke ducts or air ducts that penetrate fire compartment elements (Figure 19) or are part of a fire compartment wall (Figure 20) are surrounded by adequate fire seals, to a length of 1 metre on both sides, in the first case, or to the whole length in the second case. The relevant European standards on fire seals, ducts, etc. apply as well.

The central ventilation systems, apart from the fire protection requirements set by the Regulations and their specifications, must also have adequate fire seals (dampers), when they penetrate building elements of the envelope of fire compartments, as well as adequate automations that prevent the reverse course of the smoke towards the fire. (Figure 21)

Ducts carrying flammable liquids or gases are not allowed to pass through fire protected escape routes, unless protected by fire resistant materials or enclosed in special fire resistant shafts with a degree of fire resistance at least equal to that of the fire protected route.

Figure 18: Duct that passes through a building element of a fire compartment

| δομικό στοιχείο πυροδίαμερίσματος | building element of a fire compartment |
| --- | --- |
| διάκενο | interstitial space |
| άκαυστο περίβλημα | non-combustible envelope |
| σωλήνας | duct |

Figure 19:

| Τοίχος ή δάπεδο πυροδιαμερίσματος | Wall or floor of a fire compartment |
| --- | --- |
| Καπναγωγός | Flue |
| Πυροφραγμός | Fire seal |

Figure 20:

| LAYOUT | LAYOUT |
| --- | --- |
| Τοίχος πυροδιαμερίσματος | Fire compartment wall |
| Καπναγωγός | Flue |

Figure 21: Typical layout of fire resistant dampers

- Requirements for internal stairways

All internal stairways that are fire protected escape routes must be permanently built elements and surrounded by building elements with a degree of fire resistance as follows:

a) when the fire protected route serves 4 or less storeys, a degree of at least 60 minutes;

b) when the fire protected route serves more than 4 storeys, a degree of at least 120 minutes.

In buildings with 4 or more storeys, steps and landings must be constructed using non-combustible materials (Α1FL ή A2 – s1).

For buildings with more than six (6) storeys and a population of more than 50 persons per storey, it is necessary to have a special lobby on every floor, with two fire resistant doors, of class Sm in accordance with ΕΝ13501-2, at the entrance of the stairway, in order to keep the smoke out of the stairway. The building elements of the envelope of this lobby must have the same degree of fire resistance that is required for the stairway, while the door leading from the lobby to the staircase must have a degree of fire resistance of at least 30 minutes. The requirement for a fire protected lobby per category of use, in addition to this general requirement, is shown on Table 11.

In every building with six or more above ground storeys including the ground floor, and if it is required to have an automatic fire detection system, there must be one or more smoke exhaust dampers (Figure 22) installed above the floor of the highest storey of a stairway - at the top of the wall or on the ceiling of the highest storey, with the smoke being directly led towards the open air. Any such damper must have an unobstructed surface of at least 1.5 m2 and be automatically activated by the fire detection system.

Table 11: Requirement for the construction of a fire protected lobby

| GENERAL REQUIREMENT |  |  |
| --- | --- | --- |
| Buildings with more than 6 storeys and a population of more than 50 persons per storey |  |  |
| ADDITIONAL REQUIREMENTS |  |  |
|  | BUILDING USE | Requirement for the construction of a fire protected lobby with 2 fire resistant doors |
| B | Temporary accommodation | Hotels > 2 floors and total number of beds >100 |
| E | Health & social welfare | Every underground storey of the building |
| G | Commerce | Buildings with more than three storeys |
| H | Offices | Buildings with more than six above ground storeys, irrespective of population |
| Ι | Industry - Small crafts industry | Ζ3 Buildings |
|  |  | Buildings with more than three storeys |
| J | Storage | Ζ3 Buildings |
|  |  | Buildings with more than three storeys |
| K | Parking areas & petrol stations | Buildings with more than one underground storeys |
|  |  | Buildings with more than two above ground storeys |

Figure 22: Smoke exhaust damper

| Ελεύθερο άνοιγμα απαγωγής καπνού | Free opening for smoke exhaust |
| --- | --- |

- Requirements on external stairways

A permanent external stairway may be a fire protected escape route if it is separated from the building by building elements bearing the degree of fire resistance that is required for the fire protected escape route of the building. The steps and landings of an external stairway must be constructed out of non-combustible material (Α1FL ή A2FL – s1). The fire resistance of external walls must extend beyond both sides of the stairway by at least 2 metres. (Figure 23)

Figure 23: Fire resistance of external walls - doors and its extension for external stairways

| (όхι υπό κλίμακα) | (not in scale) |
| --- | --- |
| 2μ. | 2m. |
| Πυράντοχη θύρα | Fire resistant door |

- Requirements for walls with horizontal exits

In case of fire compartments that communicate with a horizontal exit, the degree of fire resistance of the separating wall that bears the horizontal exit must be at least 120 minutes without the possibility of reduction due to the presence of an automatic water based fire extinguishing system (water sprinklers). In addition, if there are walls on the separating element of fire compartments in an angle smaller than 180ο, there must be a degree of fire resistance of 60 minutes for a distance of at least two metres from the common wall that bears the horizontal exit. (Figure 24)

Figure 24: Extension of fireproof walls of fire compartments communicating with a horizontal exit

| Π 1 | Π 1 |
| --- | --- |
| 2,00 μ. | 2.00 metres |
| Δ.Π. 120 λεπτών | degree of fire resistance 120 minutes |
| οριζόντια έξοδος | horizontal exit |
| χωρίς απαίτηση πυροπροστασίας | no fire protection requirement |

- Requirements for lifts

The envelope of lifts' shafts must have a degree of fire resistance of at least 60 minutes, unless they are included in a fire protected staircase. At the top of the shaft there must be a smoke exhaust opening with a surface area of at least 0.10m2.

- Requirements for external escape routes

The external horizontal and vertical escape routes are considered fire protected if they are built in a fire protected way, do not contain combustible materials and are separated from the building by building elements with a degree of fire resistance at least equal to the one defined in Table 7.

- Requirements for ramps

The same requirements that apply to stairways also apply to internal or external ramps. Ramps must be constructed (inclination, landing, etc.) according to the applicable building requirements.

- Requirements on smoke and heat exhaust ventilation

#### The installation of a smoke and heat exhaust ventilation according to the relevant requirements of the EN-12101 standard is necessary in the following cases:

a. Underground parts of buildings with a surface area of more than 200 m2

b. Buildings taller than 23 metres

c. Covered patios of more than 2 storeys including basements or ground floors

d. Category B areas of risk (see 6.7)

Especially for underground areas, ventilation must preferably be natural but when it is impossible to install the ventilators outside the building, they must be installed internally, on the perimeter of the basement at a suitable distance to each other.

The requirement of point a above does not apply to detached house basements as well as underground parts that have external doors and/or windows whose surface covers at least 2.5% of the surface of the part they serve if they are in direct contact to the surroundings.

The following requirements apply especially to the underground areas referred to in point a:

- Natural ventilation

Preferably, ventilation should be natural. The required minimum surface area of the ventilation openings must be 2.5% of the surface area of the underground part they serve.

The ventilation openings are installed evenly high on the walls of the spaces.

Every category B area of risk must have a separate opening. Also, in case the underground floor is separated into areas, each part must have a separate opening, so that it is not necessary to create internal (intermediate) openings on frames, such as doors and/or windows.

It is not allowed to place ventilation openings where they might obstruct escape routes and final exits.

Every such opening must open close to the ground level.

Additional protective measures must be taken, such as prevention of obstruction of the openings, use of non-combustible grids and proper signs.

- Mechanical ventilation

Alternatively, instead of a natural ventilation system, it is allowed to install a mechanical ventilation system, if the underground area is equipped with an automatic water sprinkler system. In that case, the mechanical system must provide air renewal 10 times per hour and be able to keep the temperature of smoke below the 300ο for at least one hour.

- Flues

When flues are used, the fire resistance of their envelope must not be less than the one of the parts they penetrate.

In covered patios of up to 18 metres high, it is necessary to install a natural ventilation system on the ceiling. The total surface area of the ventilation openings must be at least equal to 10% of the largest surface area on the layout of the patio.

In addition, all covered patios are required to have a mechanical ventilation system installed in order to ensure that the total air volume shall be renewed five times per hour.

- Areas of risk

Areas of risk must be autonomous fire compartments and have a fire resistant envelope with a degree of fire resistance equal to the one required for the building's fire compartments and not less than 60 minutes. Also, areas of risk must not be placed under or in close proximity to the final exits of buildings.

In case of areas of risk, special care must be taken to avoid the spread of smoke (proper ventilation, self-closing doors, joints obstructions, etc.) .

Areas of risk are divided in the following two categories based on which the required active fire protection means are defined.

- Category Α.

- General warehouses

- Central linen rooms

- Chiller rooms, pump rooms, machine rooms

- Heating furnace areas and/or boiler rooms with a thermal power of50 kW

- Areas which, due to the nature of their contents, present a hazard and have a pyrothermal density less than or equal to 2000 MJ/m2.

- Category B.

- Heating furnace areas and boiler rooms with a thermal power of >50 KW

- Waste collection areas and/or incinerators

- Liquid gas and natural gas areas, as defined in the relevant

regulations.

- Power transformers (medium voltage and high voltage) areas, generators, electric power rooms, areas of charging points for electric vehicles.

- Warehouses for flammable materials and objects.

- Spaces which, due to the nature of their contents, present a hazard and have a pyrothermal load density greater than 2000 MJ/m2.

Table 12 shows any additional areas of risk in specific use buildings, as well as their classification in category A or B.

In any case, if during the design of a building it is established by the responsible engineer that individual spaces, that are not specifically mentioned in this Regulation, may present a high fire risk due to the nature of their contents or their increased installed power, they are treated according to the provisions that apply for areas of risk.

Table 12: Additional areas of risk per building use

| BUILDING USE |  | Category A areas of risk | Category B areas of risk |
| --- | --- | --- | --- |
| A | Residence | General requirements | General requirements |
| B | Temporary accommodation | General requirements | General requirements |
| C | Public assemblage areas | Maintenance-service areas, including areas for carpentry or dye works | General requirements |
|  |  | Film screening rooms |  |
| D | Education | Storage rooms for flammable liquids used for laboratory tests | General requirements |
|  |  | Maintenance-service areas, including areas for carpentry or dye works |  |
| E | Health & social welfare | Laboratories | Boiler room |
|  |  | Maintenance-service areas, including areas for carpentry or dye works | Storage or paint application areas, Central warehouses |
|  |  | Storage rooms for paints, central warehouse | Locker room cloak rooms |
|  |  | Central kitchen Dirty linen collection areas | Laundry room |
|  |  | Areas with a surface of up to 50 m2: - department of nuclear medicine - microbiological/biochemical/hematological/pathoanatomical complex and other relevant laboratories - laundry - central linen room - central pharmacy - waste collection/incineration/removal - central kitchen - central warehouse - maintenance-service laboratories - central sterilization | Areas with a surface > 50 m2: - department of nuclear medicine - microbiological/biochemical/hematological/pathoanatomical complex and other relevant laboratories - laundry - central linen room - central pharmacy - waste collection/incineration/removal - central kitchen - central warehouse - maintenance-service laboratories - central sterilization |
|  |  | Storage areas for cleaning products | Central linen room |
|  |  | Paraffin spa areas | Storage rooms for combustible or flammable liquids and gases used in laboratory tests |
|  |  | Shops larger than 15 m2 and shop storage rooms larger than 50 m2 |  |
|  |  | Overnight stay and day care rooms in residence units for dependent people and psychiatric treatment centres |  |
|  |  | Occupational therapy centres |  |
|  |  | Libraries |  |
|  |  | Archive rooms |  |
|  |  | X-ray storage rooms |  |
| F | Penitentiary | General requirements | General requirements |
| G | Commerce | General requirements | General requirements |
| H | Offices | Main archive storage areas | General requirements |
| Ι | Industry - Small crafts industry | Storage rooms for flammable materials | General requirements |
| J | Storage | Storage rooms for flammable materials | General requirements |
| K | Parking areas & petrol stations | Storage rooms for flammable materials | General requirements |

- Fire reaction requirements

Fire reaction requirements apply to construction products (internal finishings, floor coatings, duct thermal insulation, electric cables) that may be directly exposed to fire and aim at reducing the speed of fire spreading and the speed of smoke and flaming particles and droplets production (see Annex D).

The minimum fire reaction requirements for internal finishings, per category of use, are shown on Table 13, whereas the minimum requirements on fire reaction for electric cables are shown in Table 14.

The minimum reaction to fire requirements for linear tubing thermal insulation products are equivalent to those applicable to the interior finishes of the spaces they run, as defined in ELOT EN 13501, with an L index (A2L-s1, d0, BL-s1, d0, etc.).

Table 13: Minimum fire reaction requirements for internal finishings and floors per use category

|  | Use category |  | Walls and ceilings |  |  |  | Interstitial spaces and ceilings | Floors |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Fire protected escape routes - dangerous areas | Unprotected escape routes | General |  |  | Fire protected escape routes - dangerous areas | Unprotected escape routes |
| A | Residences |  | A2-s1, d1 | C-s1,d1 | Areas >10 m2 | Areas ≤10 m2 | C-s1,d0 | BFL-s2 | DFL-s2 |
|  |  |  |  |  | C-s2,d2 | D-s2,d2 |  |  |  |
| B | Temporary accommodation |  | A2-s1, d1 | C-s1,d1 | Rooms ≤15 m2 | Rooms >15 m2 | C-s1,d0 | BFL-s2 | CFL-s2 |
|  |  |  |  |  | D-s2,d2 | C-s2,d2 |  |  |  |
| C | Public assemblage areas |  | A2-s1, d1 | C-s1,d1 | Areas ≤30 m2 | Areas >30 m2 | C-s1,d0 | BFL-s2 | CFL-s2 |
|  |  |  |  |  | D-s2,d2 | C-s1,d1 |  |  |  |
| D | Education |  | A2-s1, d1 | C-s1,d1 | Rooms ≤ 40 m2 | Rooms > 40 m2 | C-s1,d0 | BFL-s2 | CFL-s2 |
|  |  |  |  |  | D-s2,d2 | C-s1,d1 |  |  |  |
| Ε | Health & social welfare |  | A2-s1, d1 | C-s1,d1 |  |  | B-s1,d0, | BFL-s1 | CFL-s1 |
| F | Penitentiary |  | A2-s1, d1 | C-s1,d1 |  |  | C-s1,d0 | BFL-s2 | CFL-s2 |
| G | Commerce |  | A2-s1, d1 | C-s1,d1 | Areas >10 m2 | Areas ≤10 m2 | C-s1,d0 | BFL-s2 | CFL-s2 |
|  |  |  |  |  | C-s1,d1 | D-s1,d1 |  |  |  |
| H | Office |  | A2-s1, d1 | C-s1,d1 | Areas ≤30 m2 | Areas >30 m2 | C-s1,d0 | BFL-s2 | CFL-s2 |
|  |  |  |  |  | D-s2,d1 | C-s2,d1 |  |  |  |
| Ι | Industry - Small crafts industry | Z1-Z2 | A2-s1, d1 | C-s1,d1 | Areas >10 m2 | Areas ≤10 m2 | C-s1,d0 | BFL-s2 | CFL-s2 |
|  |  |  |  |  | C-s1,d1 | D-s1,d1 |  |  |  |
|  |  | Z3 | A2-s1, d1 | B-s1, d1 | Areas >10 m2 | Areas ≤10 m2 |  | A2FL-s2 | BFL-s2 |
|  |  |  |  |  | B-s1,d1 | C-s1,d1 |  |  |  |
| J | Storage | Z1-Z2 | A2-s1, d1 | C-s1,d1 | Areas >10 m2 | Areas ≤10 m2 | C-s1,d0 | BFLl-s2 | CFL-s2 |
|  |  |  |  |  | C-s1,d1 | D-s1,d1 |  |  |  |
|  |  | Z3 | A2-s1, d1 | B-s1, d1 | Areas >10 m2 | Areas ≤10 m2 |  | A2FL-s2 | BFL-s2 |
|  |  |  |  |  | B-s1,d1 | C-s1,d1 |  |  |  |
| K | Parking areas & petrol stations |  | A2-s1, d1 | C-s1,d1 | Areas >10 m2 | Areas ≤10 m2 | C-s1,d0 | BFL-s2 | CFL-s2 |
|  |  |  |  |  | C-s1,d1 | D-s1,d1 |  |  |  |

Table 14: Minimum fire reaction requirements for electric cables per building use category

| Category | Use |  | Euroclass |
| --- | --- | --- | --- |
| A | Residence | Private and public spaces (buildings with up to 20 storeys) | Ε |
|  |  | Buildings with more than 20 storeys General | Dca-s2, d2, a2 |
|  |  | Buildings with more than 20 storeys Fire protected escape routes | B2ca-s1, d1, a1 |
| B | Temporary accommodation | General | Dca-s2, d2, a2 |
|  |  | Fire protected escape routes | B2ca-s1, d1, a1 |
| C | Public assemblage areas | General | Dca-s2, d2, a2 |
|  |  | Fire protected escape routes | B2ca-s1, d1, a1 |
| D | Education | General | Dca-s2, d2, a2 |
|  |  | Fire protected escape routes | B2ca-s1, d1, a1 |
| E | Health & social welfare | General | Dca-s2, d2, a2 |
|  |  | Fire protected escape routes | B2ca-s1, d1, a1 |
| F | Penitentiary | General | Dca-s2, d2, a2 |
|  |  | Fire protected escape routes | B2ca-s1, d1, a1 |
| G | Commerce | General | Dca-s2, d2, a2 |
|  |  | Fire protected escape routes | B2ca-s1, d1, a1 |
| H | Offices | Private and public spaces (buildings with up to 20 storeys) | Ε |
|  |  | Buildings with more than 20 storeys General | Dca-s2, d2, a2 |
|  |  | Buildings with more than 20 storeys Fire protected escape routes | B2ca-s1, d1, a1 |
| Ι | Industry - Small crafts industry | General | Dca-s2, d2, a2 |
|  |  | Fire protected escape routes | B2ca-s1, d1, a1 |
| J | Storage | General | Dca-s2, d2, a2 |
|  |  | Fire protected escape routes | B2ca-s1, d1, a1 |
| K | Parking areas & petrol stations | General | Dca-s2, d2, a2 |
|  |  | Fire protected escape routes | B2ca-s1, d1, a1 |

- Fire spread outside the building - Requirements on external building elements.

The fire may spread to an adjacent building through a separating wall or to a nearby building by way of radiation emitted from the respective external wall or even through the roof.

In adjacent buildings both walls that are in contact must have the same degree of fire resistance as the one required for the fire compartment of the building to which they belong.

The external walls on both sides of a wall separating adjacent buildings and along a distance of 0.70 metres (including the thickness of the separating wall) must not have any openings and must ensure a degree of fire resistance that is at least equal to the one required for the respective separating wall.

In case the angle of the external walls of adjacent buildings is less than 180ο, the arc length of a circle whose centre is the top of the angle and whose radius is the distance between the nearest frame and the angle's centre line must not be less than 1.10 metres (Figure 25).

The requirements of Table 15 apply for external walls of buildings from of to which there is a risk of fire spread.

The roofing elements (roofs and flat roofs) are parts of the external envelope of the building and are treated, from a fire protection perspective, as horizontal external walls. Therefore, Table 15 applies in relation to the spread of fire between buildings, especially in case one building is taller that the adjacent building.

Table 15 does not apply to tall buildings in relation to the reaction to fire class of an external lining, for which the minimum requirement is set at A2-s1d0 regardless of use and distance from the boundaries of the plot or from another building.

Figure 25: Minimum distance requirements between openings of different fire compartments

Table 15: Minimum requirements on the control of external fire spread

| Requirements on the control of external fire spread(1) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Requirement | Wall distance from the plot's limit or from another building |  |  |  |
|  | 3 metres | 3-5 m | 5-10 m. | > 10 m. |
| a) Degree of fire resistance of external wall | full(2) | full | half | no requirement |
| b) Category of fire reaction of the external coating | B-s1,d1 | B-s1, d2 | C-s2,d2 | D-s2,d2 |
|  | A2-s1d0(4) | A2-s1d1(4) | B-s2, d2(4) | C-s2, d2(4) |
| c) Percentage of openings(4) | 15% | 25% | 50% | 80% |

(1)	For high risk areas, the distance is doubled.

(2)	The required for a firewall wall in accordance to the flame spread test.

(3)	The allowed maximum percentage of openings in the total surface of the external wall is doubled if the frames have a fire resistance index of at least 30 minutes (EI 30).

(4)	Requirement for E1 and E3 subcategory buildings of health and social welfare use or buildings with a theoretical population of more than 1000 persons or buildings housing public and private schools.

The distance (a) of openings in external masonry that belongs to different fire compartments must be at least 1.40 metres, if the openings do not have the necessary degree of fire resistance. The same minimum distance applies in the case of higher fire compartments, between the highest point of the lower opening and the lowest point of the top opening, including the extension (Figure 26) and always provided that the openings do not have the degree of fire resistance that is required for the fire compartment.

In the latter case, the middle wall and the extension must have a degree of fire resistance at least equal to the one required for the fire compartment's floor. (Figure 27)

Figure 26: Distance between openings in external masonry

| τοίχος πυροδιαμερίσματος | fire compartment wall |
| --- | --- |
| Δάπεδο πυροδιαμερίσματος | fire compartment floor |

Figure 27:

| Δάπεδο πυροδιαμερίσματος | fire compartment floor |
| --- | --- |
| TOMH | CROSS-SECTION |

# Article 7: Active fire protection means

### General

The active fire protection means that are installed in buildings are defined by their specific use in relation to its metric characteristics (total gross surface it covers).

1. In the case of multi-use buildings, the active fire protection means are applied as follows:

a) If the individual uses are separate, each one of them is provided with the respective fire protection means to the whole of its surface.

b) If the mixed uses use the same-common unprotected escape routes (horizontal or vertical), i.e. they are parts of the same storey or different storeys that communicate vertically in an unprotected manner, then for the whole storey in the first case or the whole fire compartment in the second, the least optimal fire protection means for each use apply.

c) Since all of the using areas involved are fire-resistant separated and they use the same vertical fire-protected escape routes, meaning that they are parts of different floors which evacuated through the same fire-protected vertical escape routes, then the relevant fire protection means shall apply to each particular surface which it occupies respectively.

d) The active fire protection means are defined by the total surface area covered by each use in the building, even if the use is distributed in different levels, except for the case where the same uses are separated (in a fire resistant way with their own exits).

2. In the case of single-use buildings:

a) If there are complementary uses not used in full, the predominant use is followed in relation to the fire protection means as well.

b) If there are complementary uses used in full, they are provided, to the surface they cover, with their own fire protection means, whereas the rest of the building makes use of the fire protection means that are intended for the predominant use.

### Requirements on the active fire protection means, preventive means of fire protection, provision of training and information to staff members and maintenance

For the purposes of this Regulation:

- Permanent systems of active fire protection means an automatic system of fire detection, a manual system of fire alarm notification, an automatic system of flammable gases detection, automatic fire extinguishing systems (using water, powder, foam, carbon dioxide, gases, or condensed aerosols, a system of water sprayers or water sprinklers), the permanent fire-fighting water supply network and the local fire extinguishing system.

The automatic system of flammable gases detection must fulfil the requirements of parts of the EN 60079-29 standard.

- Portable and other means of active fire protection are fire extinguishers (portable, mobile, automatic ceiling mounted fire extinguishers), the simple fire-fighting network (fire cabinet), as well as autonomous smoke detectors that fulfil the requirements of the ΕΝ 14604 standard in its current version.

- Preventive means of passive fire protection are emergency lighting, safety signs and escape plans.

In all cases, the analysis, design and installation requirements for these fire fighting elements must follow the Fire-fighting Provisions (no 15/2014 (B' 3149), in their current version.

#### Fire extinguishers

##### a) Portable fire extinguishers

##### A1. Portable dry powder or water based fire extinguishers

It is necessary to install portable dry powder or water based extinguishers with a fire extinguishing ability of at least 21Α-113Β-C in all uses according to special requirements.

In case the result of the calculation of the specific uses is a decimal number, it is rounded to the nearest whole number.

Irrespective of calculations, the minimum number of fire extinguishers must not be less than two (2).

- A2. Portable carbon dioxide fire extinguishers

It is necessary to install portable carbon dioxide fire extinguishers with an extinguishing ability of at least 55B-C in areas intended for electromechanical facilities, such as medium or high voltage transformers and boiler rooms, in such positions that no part of these areas is further than 15 metres horizontally from any such fire extinguisher. In any case, the minimum number of carbon dioxide fire extinguishers in these areas must not be less than two (2).

##### b) Wheeled fire extinguishers

Wheeled fire extinguishers shall, if required, be dry dust or water base, with a charge of 25 kg.

##### c) Ceiling mounted fire extinguishers.

It is obligatory and necessary to install a self-priming roof fire extinguisher above the solid or liquid fuel heating burners and / or boilers with a thermal power of50 kW.

#### Automatic fire detection system

An automatic fire detection system is installed in category A areas of risk (see 6.7). In cases where the special provisions provide installing an automatic fire detection system, it must cover all areas of the building.

If special provisions provide that the whole building must be equipped with an automatic fire detection system, its activation must cause the opening of a ventilation frame placed on the top storey of the building next to the stairway. The activation of the automatic fire detection system must also activate the opening of ventilation dampers.

#### Automatic fire extinguishing system

It is necessary to have a water based or other appropriate automatic extinguishing system in the following areas:

- In category B areas of risk (see 6.7)

- In covered liquid fuel or other flammable liquids storage areas with a total capacity of over 3 m3.

### In cases of buildings where there must be an automatic water based extinguishing system (water sprinkler), in areas where it is not appropriate to use water as a fire extinguishing means, it is possible to install an automatic fire extinguishing system using another material.

The reference to building storeys when providing for the permanent active fire protection systems, the safety signs and the escape plans, also refers to the ground floor and below ground storeys, irrespective of their use (main or supplementary), unless otherwise specified in the relevant provisions.

The reference to a total covered surface refers to areas with main and supplementary use.

In case of multi-storey buildings, the storey surface refers to mixed surfaces, irrespective of the surface of the other storeys.

#### Local fire extinguishing system

A local extinguishing system shall be installed in the places of preparation of dishes using cooking hobs and hot surfaces, if required by number. 15/2014 Fire Brigade, as in force.

### Provision of training and information to staff

The organisation and provision of training and information to the staff must be done according to the Fire-fighting Provisions (no 14/2014 (B' 2434)), in their current version.

### Indicative preventive fire protection measures

To reduce the risk of fire and its rapid spread, several preventive fire protection measures must be taken. These measures are translated in specific activities, according to the specifications of the manufacturers of the devices and the special regulations. In addition to the following preventive fire protection measures, it is necessary to take any other relevant measure for the purpose of preventing the causes and reducing the risk of fire.

- The following activities are necessary:

- Thorough maintenance and regular inspections and control of the facilities and the devices according to the relevant regulations and the manufacturer's specifications.

- Deactivation of devices and facilities during non working days and hours or while the tenants are away, except for those that are absolutely necessary. Closing internal doors during these periods as well as during sleep hours.

- Placing a basin of adequate capacity in liquid fuel tanks to collect any leaks.

- Keeping heating devices at an adequate distance from combustible materials and properly affix the devices.

- Marking of materials and areas of risk.

- Inspection by a responsible employee of all areas after the end of activities as well as during working hours, to identify and eliminate any possible causes of fire.

- In outdoor areas that fall within the scope of this Regulation, it is necessary to clear the undergrowth and remove any useless flammable or combustible material.

- Adequate ventilation (natural or artificial) of professional storage areas.

- Proper arrangement of spaces intended for the storage of materials that can be ignited and removal of flammable and combustible materials from places where there is direct flame, sparks or other sources of heat emission.

- Placing, in a permanent way, visible signs in areas of risk informing people entering these areas that smoking is prohibited and, where necessary, warning signs that prohibit the use of water in case of fire.

- Placing, in a permanent way, signs in visible places within the facility, containing instructions for the prevention of fire and ways of reaction for the staff in case of fire.

- Regular cleaning of the areas of professional activity and immediate removal of materials that might be ignited.

- Special marking in the lifts areas of professional use buildings indicating that they should not be used in case of fire.

- Control of the proper function and status of measures and means of fire protection as well as of the closed areas to ensure the absence of a dangerous atmosphere and to guarantee proper venting, as well as removal of flammable and combustible materials before the start of heat related works.

- Ensuring that between the stored materials in warehouses or industries there is a 0.80 metres wide passage, as well as a main corridor that is at least 1.10 metres wide inside the warehouse or industry.

- Storage of materials in a way that they are at least 0.50 metres away from the ceiling.

- Storage of materials in outdoor areas of commercial stores that fall within the scope of this Regulation in such a way that the materials are at least three (3) metres away from adjacent buildings.

- Creation of the right conditions in order to avoid the accidental mixing of materials that might cause an exothermic reaction in warehouses or industries.

- Performing of evacuation drills in specific buildings at regular intervals.

- Forbidden activities:

- Permanent or temporary placement of furniture, objects and other structural assemblies on escape routes and emergency exits that may reduce their width or hamper the free circulation of the public in case of danger.

- Placement of mirrors or other objects on or near doors that might mislead people as to which is the correct way towards the emergency exit. Windows, mirrors and other structural assemblies that due to their size or construction might be confused with doors must be marked in such a way as to not be mistaken for emergency exits.

- Covering of the safety signs and the fire protection means by materials or structural assemblies.

- Decorating and covering of floors, walls and ceilings with materials that allow rapid surface flame spread.

- Use of flares, toys and fireworks in covered areas. Their use in outdoor areas is allowed without prejudice to the current legislation.

- Smoking and use of direct flame in areas of risk as well as placement of flammable materials in them.

- Smoking and use of direct flame in high risk commercial stores, industries and warehouses.

- Suspension or placement of balloons that contain flammable gases in areas frequented or used by the public.

- Installation of lights with high thermal radiation in displays that might cause fire to flammable or combustible materials without taking precautionary measures.

- Locking the doors of public exits with mechanisms that demand the use of a key to unlock.

### Use of fuel and other materials

In case liquid or gaseous fuels, or other combustible or dangerous materials are used or stored, the provisions of the relevant laws are applied additionally.

## Article 8: Standards – technical specifications – certificates

The Hellenic Organization for Standardization (ELOT) is a member of CEN/CENELEC. The standards that are referred to in this Regulation refer to the European standards that have been transposed to the national standardization system by ELOT. These standards are defined by the acronym ELOT EN XXXXX.

In case where there is no ELOT-EN standard, the international ISO/IEC standards apply. In cases that these are not or are only partly adequate, it is allowed to apply national standards of other countries, preferably from the European Union.

The ELOT standards on passive fire protection are in general the ones referred to in the standards for classification of parts of the ELOT EN-13501 standard, as well as the relevant parts of the ELOT EN-12101 standard on heat and smoke control systems, as amended and applied.

The ELOT standards on active fire protection are the ones referred to in the Fire Fighting Provisions (no 15/2014), as amended and applied.

Construction products or equipment lawfully manufactured and/or placed on the market in another EU Member State or in Turkey, or lawfully manufactured and placed on the market in an EFTA State party to the EEA Agreement, may be placed on the Greek market when manufactured in accordance with standards, specifications and/or procedures for production and testing which can be demonstrated as guaranteeing a level of quality and safety equivalent to that in the requirements of this technical regulation for the protection of human health and safety and the environment.

According to the EU Regulation on Construction Products (Regulation No 305/2011 of the European Parliament and of the Council), in order for a construction product to enter the European market, it is necessary to have a CE marking. Part of the CE marking assessment criteria is the construction product's performance in relation to its resistance and reaction to fire. The developer is obliged to keep records with the certificates of materials and building elements that are installed in the building. By activating the electronic identification of buildings, these certificates are placed in the relevant electronic file of the building and are integral parts of it.

By the decisions of the competent Minister, as the case may be, determine the relevant Greek standards of ELOT (Greek Tourist Authority) with which all of the constructions, construction products and products of active and passive fire protection, certificates of conformity, control procedures and laboratory tests of fire reaction and fire resistance must comply. With similar decisions categories, levels and performance values are determined in the construction products, building elements and constructions for which no laboratory tests are required, as well as any other technical provision concerning compliance with EU law in the field of fire safety and fire protection of buildings are defined by similar decisions.

# CHAPTER B: SPECIAL PROVISIONS

## Article 1: Residence

## Article 2: Temporary accommodation

## Article 3: Public assemblage

## Article 4: Education

## Article 5: Health & social welfare

## Article 6: Penitentiary

## Article 7: Commerce

## Article 8: Offices

## Article 9: Industry - Small crafts industry

## Article 10: Storage

## Article 11: Parking areas & petrol stations

In articles 1 to 11 of this Chapter special provisions on the fire protection of the individual uses of buildings are defined, in addition to the general provisions of Chapter A.

## Article 1: Residence

- General

This category includes all buildings or parts of buildings that are used as residences, as they described in the Table of Annex A’ of the present Regulation.

Indicative complementary uses in this category are small warehouses, small offices, etc.

The provisions of article 4, par. 4.2.2, subparagraph iii of Chapter A on mixed uses do not apply for this category of buildings.

- Design of escape routes

The minimum width of the escape route is set to 0.80 metres.

The minimum unobstructed width for the doors of the escape routes until reaching a common corridor may be 0.70 metres.

The maximum length of a real route is set in Table 5 of Chapter A. It is necessary to provide for at least two escape routes that end up to respective emergency exits in:

a) storeys with a population of over 50 persons.

b) apartment buildings with more than 6 floors and a population per storey of over 30 persons.

- Structural fire protection

In cases of multi-use buildings that are used as residences, if their uses are not separated, the common part of the route (corridor) that serves the residence up to the emergency exit in the fire protected stairway must be fire protected and have the least optimal degree of fire resistance of the respective mixed uses.

In cases where it is necessary to have fire resistant doors in every residence, these are allowed to have a degree of fire resistance that is 30 minutes less than the degree of fire resistance of the building and, in any case, at least 30 minutes.

- Emergency lighting, safety signs and escape plans.

In apartment buildings, emergency lighting must be installed on all escape routes, common areas and emergency exits.

There must be safety signs in Escape routes, common areas, emergency exits and fire fighting equipment.

- Preventive measures and necessary actions.

- Conformity with the specifications of the manufacturer of heating appliances.

- Keeping adequate distance between heating appliances and combustible materials.

- Placing of a proper mesh in front of electric heaters.

- Removal of ashes using a metal shovel in fire places and wood stoves.

- Placement of a proper protective cover in front of the fire place opening.

- Placing of fire resistant building elements-floors next to the opening of the fire place and placement of the wood stove on a fire resistant base-floor.

- Regular cleaning of chimneys.

- Regular checks of ducts and other heating assemblies using liquid or gaseous fuel.

- Turning off heaters and other heating appliances before exiting the residence or before sleep.

- Forbidden activities

- Placing heating devices on carpets.

- Adding flammable liquids in fire places or wood stoves.

- Placing combustible small objects on the fireplace mantel.

- Moving a liquid gas stove while in operation.

- Filling up an oil stove with fuel while in operation or while it is still hot.

- Storage of combustible objects (i.e. firewood, home equipment, etc.) in boiler rooms or fuel storage rooms.

- Active fire protection means

- Portable fire extinguishers dry powder or water based

There must be one (1) portable fire extinguisher in every common room of every storey. Each fire extinguishers must cover a gross surface area of 400 m2, otherwise additional fire extinguishers are needed. There must be a portable fire extinguisher in every detached house irrespective of its surface area.

- Manual alarm system

A manual alarm system must be installed in apartment buildings with three (3) or more main use storeys. The announcement buttons must be placed in the common routes next to stairways.

- Fire detection

It is necessary to install an automatic fire detection system. By way of exception, in residence buildings with three (3) or less main use storeys, instead of an automatic fire detection system it is allowed to place portable fire detectors according to the manufacturer's specifications, covering at least every bedroom and the kitchen.

- Permanent fire-fighting water supply network

A permanent fire-fighting water supply network must be provided in apartment buildings higher than 28 metres with a total storey surface of more than 500 m2.

## Article 2: Temporary accommodation

- General

This category includes all tourist facilities that are used to provide to their tenants rooms intended for sleeping and personal hygiene, and have a capacity of at least 20 beds. Facilities with a capacity of less than 20 beds fall under the scope of buildings that are used for residence.

Indicative complementary uses in this category are warehouses, offices, breakfast areas, events hall, restaurants, beauty parlours, gyms, etc.

- Design of escape routes

The minimum allowed width of escape routes, as well as the width of the doors of emergency exits is set to 0.90 metres. In any case, the minimum free width for the doors of escape routes must be 0.80 metres.

In addition to the general provisions, the number and width of the emergency exits in every storey are set according to the following table:

| NUMBER AND WIDTH OF EMERGENCY EXITS ON EVERY STOREY |  |  |
| --- | --- | --- |
| Theoretical population | Minimum number of exits | Minimum width of all exits |
| Up to 50 | 1* | 0.90 metres |
| 51 - 250 persons | 2 | 1.10 metres |
| 251 - 500 persons | 2 | 1.40 metres |
| 501 - 750 persons | 3 | 1.60 metres |
| 751 - 1000 persons | 4 | 1.80 metres |

*By way of exception, in underground main use areas as well as in buildings with three or more main use storeys, there must be at least two (2) emergency exits with a minimum width of 0.90 metres.

For a population of more than 1,000 persons, there must be an additional exit 1.80 metres wide for every 250 people or a fraction of that.

In emergency exits, no mirrors may be placed that might cause confusion as to the direction of the escape route and, in general, it is not allowed to place furniture or other obstacles that obstruct the route.

Every door must have the right equipment so that it may open automatically towards the direction of the escape route. If there are locks, they must be of a type that does not necessitate the use of a key in order to open towards the right direction.

- Structural fire protection

Indoors stairways in hotels with three or more storeys must be fire protected.

The doors of accommodation units leading to common corridors must be fire resistant and have a degree of fire resistance of at least 30 minutes.

- Emergency lighting, safety signs and escape plans.

Emergency lighting must be installed on all escape routes and emergency exits.

Escape routes, emergency exits and fire fighting equipment must be provided with safety signs.

Escape diagrams must be placed on the wall in all accommodation units, common areas and the other main use areas, such as public assemblage areas.

- Active fire protection means

- Portable fire extinguishers dry powder or water based

There must be one (1) fire extinguisher per 100 m2 of gross surface.

- Manual alarm system

All buildings of this category must be equipped with a manual alarm system.

- Fire detection

An automatic fire detection system must be provided in the following cases:

a. In temporary accommodation buildings with a total capacity of at least 50 beds.

b. In hotels with two (2) or more main use storeys.

- Permanent fire-fighting water supply network – simple fire-fighting water supply network

A permanent fire-fighting water supply network must be present:

a) In temporary accommodation buildings with three (3) or more floors of main use and a capacity of at least one hundred (100) beds.

b) In camps located within a forest or forest area or less than 300 m from forest or forest land.

Temporary accommodation buildings that are not required to install a permanent water supply network are required to install a simple water supply firenetwork (fire cabinet).

- Automatic fire extinguishing systems

An automatic fire extinguishing system (water sprinkler) must be present in the following cases:

a. In temporary accommodation buildings with over 23 m height.

b. In temporary accommodation buildings with three (3) or more main-use floors and a capacity of at least three hundred (300) beds.

## Article 3: Public assemblage

- General

The public assemblage category includes buildings or parts of buildings or areas in buildings and plots, as well as ancillary spaces, where at least 50 persons assemble to take part in social, financial, cultural, religious, entertainment, educational, scientific or athletic events and activities. More concretely, this category includes conference halls, auditoriums, waiting areas for means of transport, airport halls, sports fields, clubs, playgrounds, amusement parks, senior citizens halls, catering establishments, recreation areas and serving areas.

Buildings or areas with a theoretical population of assemblage of less than 50 persons fall under the respective specific article of the most relevant category.

Banks with a total surface of less than 70 m2, areas for the provision of services and establishments of sanitary interest, with a theoretical population of assemblage of up to 49 persons such as post offices, citizen service centres, lottery retailers, restaurants, pastry shops, cafés, bars, pizzerias, snack bars, fall under the scope of Article 7 "Commerce".

Areas destined for educational and sporting activities, such as dance schools, sports schools, gyms etc. with a population of up to 49 persons fall under the scope of Article 4 "Education".

Indicative complementary uses in this category are small offices, small warehouses, ancillary areas, small cooking areas, etc.

.

- Calculating the theoretical population

When calculating the population of a public assemblage area the following must also be taken under consideration (in addition to the General Provisions):

- A public assemblage area may be intended for a single activity or for multiple activities not performed at the same time. In that case, the area's population is considered to be the one of the least optimal activity.

- A public assemblage area may, during its operation, have different assemblage densities in its different parts, i.e. areas intended for standing people, areas with fixed or non fixed seats, etc. In that case, the population of the area is calculated by adding together the individual numbers of people assembled.

- A single space may contain areas intended for different public assemblage activities performed at the same time, for example an airport hall or a sports hall.

In that case, the population of the area is calculated by adding together the individual numbers of people assembled.

- In areas of public assemblage with no defined use, the population shall be calculated as follows: 1 person / 0.30 m2 of their floor surface. This does not apply to areas that are clearly separated by fixed elements for the circulation of the public.

- In cases where, according to other provisions, the number of assembled people in an area is higher than the number calculated according to the previous paragraphs, this higher number is considered to be the population.

- In theatres, cinemas, entertainment halls and other such areas of public assemblage, where people enter an area when there are no seats available for them but they are allowed to wait in hallways or other waiting areas until there are available seats, the following requirements must be met:

a)	The waiting area population must be 1 person / 0.30 m2 of floor surface (people standing).

b)	This waiting area population is added to the population of the assemblage area so that the total population is calculated.

c)	Care must be taken, so that people waiting are confined to areas so as not to hinder or obstruct the routes or exits and cover part of their width.

In addition to the aforementioned, to calculate the population in buildings used for public assemblage where there is a covered patio, the following apply:

For areas intended for the circulation of people with a gross surface of up to 14,000 m2, the theoretical population factor is set to 2.8 m2 per person.

For a gross surface of more than 14,000 m2, the factor is set to 3.3 m2 per person. This value is increased by 0.1 for every 1,000 m2 above 14,000 m2 or a fraction of these.

The used areas that are served by the above mentioned circulation areas of the covered patio must be provided with independent emergency exits and for the design purposes, they must be considered as parts of the escape routes.

- Design of escape routes

- Number and width of emergency exits

In addition to the general provisions, the number and width of the emergency exits in every storey are set according to the following table:

| Number and width of emergency exits per storey |  |  |
| --- | --- | --- |
| Theoretical population | Minimum number of exits | Minimum width of all exits |
| 50-150 persons | 2 | 0.90 |
| 151-300 persons | 2 | 1.40 |
| 301-500 persons | 2 | 1.80 |
| 501-800 persons | 3 | 1.80 |

For a population of more than 800 persons, there must be one (1) additional emergency exit that is 1.80 metres wide for every 300 persons or a fraction of that.

In case the fire compartment is equipped with an indoor balcony that is not considered as a separate storey, then, if the theoretical population of its surface is more than 49 persons, it must have two alternative routes.

The exits must be at a distance from each other and placed in such a way as to minimize the possibility of obstructing at the same time the routes that lead towards more than one exits in case of fire.

- Requirements for areas with fixed seats

In public assemblage areas with fixed seats, the following requirements must also be met:

a) At the end of every row of seats there are longitudinal aisles or emergency exits.

Especially in areas with fixed seats which are placed in consecutive levels of the floor with a minimum difference between levels of 0.35 metres and are used either directly as seats (athletic field stands, theatre stands, etc.) or in order to place other seats on them, the width of each level must be set at least to 0.85 metres.

b) the minimum width of longitudinal and transversal aisles is set to 0.90 metres in aisles without levels and to 1.10 metres in aisles with levels. Aisles with an inclination of less than 1:8 shall be constructed in the form of ramps; if their inclination is higher shall be constructed in the form of stairs.

c) The number of fixed seats in rows of seats accessed via a longitudinal aisle or via two longitudinal aisles depends on the unobstructed horizontal distance (Ι) between seats of consecutive rows measured either with folding or with non-folding seats (Figure 28) and is according to the following table:

| Number of seats in one row |  |  |
| --- | --- | --- |
| Unobstructed horizontal (I) distance (in m.) | Maximum number of seats in one row |  |
|  | One longitudinal aisle | Two longitudinal aisles |
| 0.30 to 0.324 | 7 | 14 |
| 0.325 to 0.349 | 8 | 16 |
| 0.35 to 0.374 | 9 | 18 |
| 0.375 - 0.399 | 10 | 20 |
| 0.40 - 0.424 | 11 | 22 |
| 0.425 - 0.449 | 12 | 24 |
| 0.45 - 0.474 | 12 | 26 |
| 0.475 - 0.499 | 12 | 28 |
| >0.50 | 12 | Without limitation as long as the provision on the maximum unprotected escape route is met and the longitudinal aisles lead to a direction opposite to the stage area or to the part of the area that is of interest to the viewers. |

Figure 28: Typical lay out of fixed (non folding) and folding seats

a) Non folding seats b) Folding seats

- Emergency lighting, safety signs and escape plans

Emergency lighting must be installed on all escape routes and emergency exits.

Emergency lights in covered and/or open entertainment halls, theatres and cinemas must have a luminosity of at least 2 lux in open areas and 5 lux in escape routes. In all other cases, the requirements of the ELOT EN 1838 standard apply.

Escape routes, emergency exits and fire fighting equipment must be provided with safety signs.

Escape diagrams must be placed on the walls in public assemblage areas, whose main use covers four or more storeys.

- Special requirements for theatre stages and film screening rooms

- Theatre stage

- Every theatre stage is equipped with a suspended balcony or a fly system or scaffolding that is used for mobile scenery and every closed stage whose floor surface is larger than 60 m2 must be provided with an automatic water sprinkler system or other systems of water sprinkling or spaying.. The sprinklers are placed under the ceiling, under the fly system, in the trap room, in ancillary areas, in the dressing rooms, in the storage rooms and in laboratories that are used for theatre purposes. The sprinklers must be placed on the perimeter of all openings to the floor of the stage.

- In stages with a floor surface of more than 60 m2, there must be natural ventilation openings with an active ventilation surface for the exhaust of smoke and hot fumes that is at least equal to 5% of the stage floor. This ventilation system must function manually or automatically using an automatic mechanism activated by heat and smoke. In case there is a mechanical ventilation installation, the above requirement on natural ventilation must be met irrespective of the function of ventilation machinery.

- The opening of every stage with a floor surface above 100 m2 must be equipped with a fire resistant curtain. The curtain is constructed and installed in such a way that when closed it prevents hot fumes, flames and smoke from entering the viewers' area for a time frame of at least five (5) minutes and offers protection from radiation due to a fire on stage.

The curtain must close automatically.

Instead of the above provisions, the following may be applied at the same time:

  - A curtain made of non-combustible non-transparent fabric with an automatic closing mechanism.

  - An automatic water sprinkler system placed on both sides of the curtain. The curtain must be kept wet in its whole surface for at least 30 minutes. The water supply is controlled by a suitable valve.

  - The curtain, the curtain's sprayers, the stage sprinklers and the ventilation openings must be automatically activated in case of fire.

  - The protection systems must be also manually activated via a control on the fire control station.

  - When the control valve of the sprinklers or sprayers is activated, the fire control station shall receive a signal upon which the ventilation system shall be automatically activated and the curtain shall close.

- In the area within or next to the stage, there is a fire control station equipped with the following:

- Luminous signs informing about the emergency lighting and the energy supply networks.

- Manual switches controlling the curtain sprayers and the ventilation.

- The control system for the sprinklers.

- Two alarm systems: one for the stage area and one for the public.

- The control room of the stage's electromechanical facilities must be surrounded by fire resistant building elements with a degree of fire resistance equal to the one that is necessary for the building's storey.

It is forbidden to install there the main lighting panels and the emergency lighting panels for the rest of the theatre areas.

- The openings that are used for communication with the stage must be fire resistant (for at least 30 minutes) and self-closing. Laboratories and storage areas of flammable materials may not communicate with the stage.

- There shall be at least two fire-fighting nests installed on each side on each tent, if a fixed water main is required, otherwise at least two cabinets of a single water-fired fire main shall be installed. There must also be portable dry powder or water based fire extinguishers (at a rate of one per 60 sq.m. floor).

- In stages with a floor surface smaller than 60 m2, it is not necessary to fulfil the above mentioned requirements but there must be at least two fire extinguishers.

- The stage must be equipped with at least two emergency exits. The same applies for the ancillary areas of the stage, as well as for the trap room, where there must be at least one exit that is independent from the stage. The maximum real distance of unprotected route for these areas is 22 metres. From there on, the escape route must be fire protected.

- Film screening rooms

These chambers must have adequate ventilation with air being supplied by at least two supply ducts and at least one exhaust outlet. The system must ensure the room's air renewal every 3 minutes. The exhaust air must end up outside the building, so that it may not re enter through the ventilation system.

- Active fire protection means

- Portable fire extinguishersdry powder or water based

There must be one (1) fire extinguisher per 100 m2 of gross surface.

- Manual alarm system

A manual alarm system must be provided in the following cases:

a. In public assemblage areas with a theoretical population of more than 250 persons.

b. In public assemblage areas where the main use covers three (3) or more storeys and/or balconies.

- Fire detection

An automatic fire detection system must be provided in the following cases:

a. In all buildings that house museums, irrespective of their surface.

b. In public assemblage areas where the main use covers three (3) or more storeys and/or balconies.

c. In public assemblage areas with a theoretical population of more than 250 persons. In addition, a public address system is placed in public assemblage areas with a theoretical population of more than 1,500 persons.

d. In covered patios. The activation of the automatic fire detection system must, additionally, lead to the activation of the mechanical ventilation system and preferably to the rapid opening of at least 50% of the surface of the patio's roof (in under 1 minute).

- Permanent fire-fighting water supply network - simple fire-fighting water supply network

A permanent fire-fighting water supply network must be provided in the following cases:

a. In public assemblage areas with a theoretical population of more than 250 persons.

b. In museums, galleries, exhibition centres and areas intended for similar activities with a total covered area of over 1,000 sq.m.

c. In public assemblage areas, whose the floor lies 20 metres above the level of the ground.

Public assemblage areas not obliged to have a permanent fire-fighting water supply network must have a simple fire-fighting water supply network.

- Automatic fire extinguishing system

An automatic water based fire extinguishing system (water sprinklers) must be installed covering the whole surface of public assemblage areas in the following cases:

a. In exhibition centre areas with a total covered surface of more than 3,500 m2.

b. In public assemblage areas with a theoretical population of more than 50 persons, whose floor lies 23 metres above the level of the ground.

c. In underground public assemblage areas with a theoretical population of more than 50 persons. The automatic fire extinguishing system covers additionally the unprotected escape routes, up to the final emergency exit.

By way of exception, it is not necessary to install the above mentioned system, if the public assemblage area is in the first (1st) basement, has a theoretical population of up to 150 persons and one (1) of its emergency exits leads directly, or via a fire protected escape route, to a safe outdoor area or road.

d) Inthe stage and ancillary areas of theatres, as described and provided in the paragraph 3.4.1.

- Special requirements for outdoor public assemblage areas

An outdoor public assemblage area is any non-covered public assemblage area, whose configuration limits the unobstructed and direct escape of the public from it (fenced area) to another outdoor safe area. In such an area, all escape routes up to the final exits do not pass through closed areas.

- Theoretical population, escape routes and emergency exits in outdoor public assemblage areas

The theoretical population of the covered area, when passing through an outdoor assemblage area is not added to the calculation for the provision of fire fighting measures and means.

The capacity of the escape route per width unit (0.60 metres) of horizontal and vertical escape routes is set to 200 persons. In outdoor public assemblage areas the notion of a fire protected escape route or that of an emergency exit do not apply and all exits leading to a safe area are considered as final exits.

The maximum length of an escape route to a final exit is 100 m.

The escape to final exits must be ensured from any point of an outdoor public assemblage area. The number and width of these final exits are presented in the following table:

| Number and width of final exits |  |  |
| --- | --- | --- |
| Theoretical population (persons) | Number of emergency exits | Exit width (in metres) |
| 50-100 persons | 1 | 0.90 |
| 101 - 450 persons | 2 | 0.90 |
| 451 - 900 persons | 2 | 1.40 |
| 901 - 1800 persons | 2 | 1.80 |
| 1801 - 2700 persons | 3 | 1.80 |

For a population of more than 2,700 persons, there must be one (1) additional emergency exit that is 1.80 metres wide for every 900 persons or a fraction of that.

Final exits must be placed at a distance to each other in such a way as to minimize the possibility of them being obstructed at the same time.

- Active fire protection means

- Portable fire extinguishers dry powder or water based

Fire extinguishers must be placed in such a way so that every point is no more than 15 metres away from the nearest fire extinguisher, and there must be at least two (2) fire extinguishers.

- Water intake points

Outdoor public assemblage areas must have an adequate number of water intake points that are connected to the water-supply network, via a 20 meter long pliable elastic hose with a suitable nozzle, so that their whole surface is covered.

- Special requirements for semi-open public assemblage areas

Semi-open public assemblage areas fall under the provisions of closed areas, except for the cases where all of the following requirements are met (in which case, the provisions on outdoor public assemblage areas apply):

a. The area is on the ground level.

b. There are no storeys above the semi-open area and its flat roof is not used. Any underground area that is not functionally related to the main use of the ground level area is an autonomous fire compartment.

c. The total surface of the semi-open public assemblage area does not exceed 500 m2.

d. There is no obstruction to the circulation and escape of the public due to smoke. Therefore:

i. All building elements of the ceiling of this area must be at least 2.65 metres above its floor.

ii. The total opening of the side surface of the area must be equal at least to 50% of it. The placement of the openings must ensure the exhaust of smoke.

## Article 4: Education

- General

This category includes buildings or parts of buildings intended for teaching, such as buildings for the provision of all levels of public and private education to students older than 5 years of age (kindergartens, primary schools, secondary schools, colleges, universities, etc.), private tuition centres, conservatoria, vocational training schools, art workshops (painting, sculpture, etc.), creative learning and play centres for children older than 5 years of age etc., without prejudice to the provisions of article 3 of this Chapter.

This category does not include crèches, pre-school facilities or boarding schools for children younger than 5 years of age, irrespective of whether they are also used as dormitories; these fall under the scope of Article 5.

Indicative complementary uses in this category are multi-use rooms, gym halls, library halls, small storage rooms, offices, conference halls, etc.

Buildings or parts of buildings used for education that are not fully used, i.e. less than 6 persons are taught in them, fall under the provisions of Article 8 of this Chapter.

- Design of escape routes

In addition to the general provisions, the number and width of the emergency exits in every storey are set according to the following table:

| Number and width of emergency exits per storey |  |  |
| --- | --- | --- |
| Theoretical population | Minimum number of exits | Minimum width of all exits |
| Up to 50 | 1* | 0.90 |
| 51 - 150 persons | 2 | 1.10 metres |
| 151 - 400 persons | 2 | 1.40 metres |
| 401 - 700 persons | 3 | 1.60 metres |
| 701 - 1000 persons | 4 | 1.80 metres |

*By way of exception, in underground main use areas, there must be at least two (2) emergency exits with a minimum width of 0.90 metres.

For a population of more than 1,000 people, an exit of 1.80 meters width per 250 people or a fraction of them is added.

The direct distance between the most remote point from the door of a teaching room and that door must not exceed 12 metres. Otherwise, one additional door must be provided. (Figure 29)

Figure 29: Special requirements on the direct distance within rooms

Every door that is part of escape routes and provides escape from a room with a population of over 30 persons must open towards the direction of escape and must be fire resistant, with a degree of fire resistance of at least 30 minutes.

When the door serves more than 50 persons, it is forbidden to have any locking system, apart from the special equipment that is suitable for panic situations.

- Structural fire protection

In buildings used for educational purposes that are taller than 15 metres, there must be provisions for a stairway and a lift to facilitate the access of fire-fighters.

Areas of risk, including cooking areas, laundry rooms and waste collection areas must be autonomous fire compartments, irrespective of their surface area, they must have ventilation openings and they must not be placed under or next to final exits.

- Emergency lighting, safety signs and escape plans

Emergency lighting must be installed on all escape routes and emergency exits.

Escape routes, emergency exits and fire fighting equipment must be provided with safety signs.

Buildings used for educational purposes, whose main use covers three (3) or more storeys or levels, must have escape plans in every main use room as well as in common rooms.

- Preventive measures and necessary actions

In laboratories where flammable liquids are used in a total quantity of over 50l, it is additionally necessary to store their containers in cabinets with a minimum degree of fire resistance equal to 30 minutes, according to the requirements of the EN 14470-1 standard.

In case more than 220l of pressurised gases are used, it is additionally necessary to store their containers in cabinets with a minimum degree of fire resistance equal to 30 minutes, according to the requirements of the EN 14470-2 standard.

- Active fire protection means

- Portable fire extinguishers dry powder or water based

There must be one (1) fire extinguisher per 150 m2 of gross surface.

- Manual alarm system

A manual alarm system must be present in buildings used for educational purposes with a theoretical population of more than fifty (50) persons.

- Fire detection

An automatic fire detection system must be provided in the following cases:

a. In buildings used for educational purposes intended for children older than 6 years of age or people with special needs (such as kindergartens, schools for the blind, etc.)

b. In buildings used for educational purposes with four (4) or more storeys including the ground floor and the basement.

c. In any physics-chemistry laboratory, computer room, archive room and library.

- Permanent fire-fighting water supply network – simple fire-fighting water supply network

A permanent fire-fighting water supply network must be provided in the following cases:

a. In building schools with four (4) or more floors and a total school area of at least 2,000 sq.m.

b. In educational establishments with a total area of at least 4,000 m².

Buildings used for educational purposes not obliged to have a permanent fire-fighting water supply network must have a simple fire-fighting water supply network (fire cabinet).

- Automatic fire extinguishing system

There must be an automatic water-based fire extinguishing system (water sprinklers) in all buildings used for educational purposes that are taller than 23 metres.

## Article 5: Health & social welfare

- General

This category includes buildings or parts of buildings that are used for medical prevention, diagnosis and treatment, for the care of older people or patients with diminished mental or physical capacity, for providing sleeping arrangements, personal hygiene and care to infants and children younger than five years of age.

The buildings that are intended for health and social welfare purposes are divided in the following sub-categories:

- Ε1: Buildings intended for welfare (social welfare), such as homes for the elderly, crèches, nurseries, boarding schools, orphanages, open day care centres and dormitories for the homeless, centres for the day care of seniors or children younger than 5 years of age, etc.

- Ε2: Buildings intended for health purposes, that have no surgical theatres or recovery or treatment beds and are only used for preventive, diagnostic or day treatment purposes without overnight stay, such as regional practices, special regional practices, health units, medical complexes, diagnostic laboratories, natural medicine and recovery centres, medical-pedagogical centres, mental health hospices, mental health day centres, social rehabilitation units, dental care complexes, multi-purpose regional practices, etc.

- Ε3: Buildings intended for health purposes, that have medical care units or surgery theatres, recovery areas, such as public hospitals and private clinics, health centres (where full basic care services are provided), chronic dialysis units, mental health centres, day medical care units, etc.

A medical careunit is an area of the building that is intended for health purposes, where there is an autonomous functional unit providing medical care to in-patients, equipped with its own nursing staff and a head nurse. It comprises in-patients rooms and all working areas for doctors and nursing staff as well as all ancillary areas that are necessary for the direct provision of medical care to patients. It is provided with one nursing station and an autonomous intracom system.

By way of exception:

a) Hospices for the transitional accommodation of homeless people fall under the scope of the article on Temporary accommodation.

b) Protected apartments for the reintegration of people with mental health issues and supported apartments for the reintegration of homeless people fall under the scope of the article on Residence.

c) Simple medical practices, regional practices and dental practices that have no nursing care beds nor an isotope application unit, an X-ray lab or physical therapy facilities fall under the scope of the article on Offices.

In case of uncertainty about the classification of a health and social care unit, the final decision is taken by the responsible Department of the Ministry of Environment and Energy, taking under consideration its structural requirements as analysed in the relevant document of the relevant department.

Indicative complementary uses in this category are catering areas, kitchens, offices, religious areas, small shops, laundry rooms, repair laboratories, storage rooms etc.

- Design of escape routes

- Width of escape routes

The minimum allowed width for the escape routes in buildings of categories E1, E2 and E3 are as follows:

- corridors 1.80 metres

- stairs, ramps 1.20 metres

- doors of sanitary facilities 0.80 metres

- other doors 0.90 metres.

By way of exception, the minimum width of corridors may be 1.20 metres fo building of class Ε1 and 1.00 metres for buildings of class E2.

In buildings of class Ε3 the minimum allowed width for escape routes in the parts that are intended for in-patients or patients receiving treatment in the emergency care unit or patients of the physical therapy department are as follows:

- corridors 2.20 metres

- stairs, ramps 1.40 metres

- doors of sanitary facilities 0.80 metres

- other doors 1.10 metres.

By way of exception, there are no obligatory minimum widths, apart from the ones required by the general provisions and the ones necessary for the respective capacities of escape routes, for corridors, stairs, ramps and doors that are not meant to be used in any case by in-patients persons or people with diminished mental or physical capacity or by older people receiving care or children younger than five years of age.

- Horizontal exits

It is also required to ensure access to a horizontal exit that is located on the same floor from any point of a medical care unit or a residence unit for dependent people. A residence unit for dependent people is part of a building intended for purposes of social welfare used for sleep and for the provision of personal hygiene services to seniors or infants or children younger than 5 years of age or people of diminished physical or mental capacity.

Each of the two areas that are interconnected by a horizontal exit must have near the horizontal exit enough space for the population of the other area - this space must have a net surface of at least 0.30 m2 per person and of 3 m2 per bed.

It is forbidden for medical care units and residence units for dependent people to communicate via a horizontal exit with any area of risk.

The unobstructed width of doors in all of the horizontal exits located on their back must conform, for each escape route direction, to the ones defined in the relevant provisions but not less than:

a) 1.10 metres, for routes serving in-patients or patients receiving treatment in the emergency care unit or patients of the physical therapy department;

b) 0.90 metres for all other cases.

- Doors – Handrails

It is forbidden to lock the doors of rooms of medical care units as well as the doors of the rooms of residence units for dependent people that lead to the inside of the building.

By way of exception to article 5 paragraph 5.3.7.3 of Chapter A, it is allowed to lock from the inside of the room the doors of the rooms of residence units for dependent people that lead to the inside of the building, when all of the following requirements are met:

a)	The people staying in the rooms are not people of diminished mental capacity or children.

b)	The doors may unlock from the outside in case of an emergency.

With the exception of the same paragraph of the general provisions, latches or other suitable access control mechanisms may be provided on the side of the door outside the chamber to the doors of the psychiatric ward or other persons with reduced mental capacity.

It must be possible to unlock all doors leading to sanitary facilities from the outside in case of an emergency.

Any door panel of a horizontal exit must have a fire resistant vision panel that ensures visibility towards the opposite direction without diminishing the necessary fire resistance of the door.

A door leading to a corridor (whose frame is vertical to the passageway axis) must have an unobstructed width not more than 0.20 metres smaller than the minimum allowed width of the corridor according to the requirements of this article. If the corridor's width is larger than the minimum necessary, this does not mean that the door must also be wider.

Handrails must be placed on both sides as well as on the landings of every stairway or ramp that is at least 1.20 metres wide and forms part of an escape route.

In corridors intended for circulation and in rooms in the medical care unit, it is allowed to install self-closing fire resistant doors that are kept open via electromagnets, if the activation of the automatic fire detection system deactivates the electromagnets and leads to the doors closing.

- Final escape exit

In buildings or parts of buildings where mental patients or other people with diminished intellectual capacity are treated, their controlled escape is allowed with escape routes leading to fenced outdoor areas that meet the following requirements:

a) They are next to a public area of the agglomeration and there are at least two doors located as far as possible from each other, of the width defined in this Regulation.

b) The doors and their locks must be constructed in such a way that they may be opened or broken into by the relevant authorities.

c) No flammable materials may be stored in this outdoor area.

d) The remaining outdoor area after the deduction of a three meter zone next to the building has a surface of at least 2 m2 per person for the population entering it.

The real distance of this unprotected escape route must not be more than 60 metres.

- Lifts for the access of fire-fighters

By way of exception to table 6 of Chapter A, in the buildings of class Ε1 and Ε2 there must be a fire-fighters lift, if the buildings are higher than 15 metres and the storey's surface is larger than 500 m2

In buildings of class Ε3 with a storey surface of more than 750 m2, there must be at least two (2) lifts.

- Structural fire protection

Medical care units and residence units for dependent people must be separate fire compartments.

It is forbidden for one medical care unit to be housed in more than one fire compartments. By way of exception, it is allowed to house one medical care unit in two fire compartments that are in contact when all of the following requirements are met:

a)	There is no other medical care unit on the same storey.

b)	For each of the two fire compartments, the requirements mentioned in point (ii) above are met concerning the horizontal exit.

c)	The door of an horizontal exit connecting the fire compartments is self-closing, but in normal operating conditions of the building can be held in the open position. As soon as a fire is detected in any of the two fire compartments, the door-holding mechanism is deactivated. In that case, the release mechanism is activated and the door closes.

Common areas of medical care units may either be a separate fire-compartment or be part of the same fire compartment with the one or more medical care units they serve.

Such common areas may be waiting rooms for visitors, living rooms for patients, offices and overnight rooms for doctors, rest rooms and locker rooms for the nursing staff, cafeterias, goods distribution areas, used goods collection areas, waste collection areas and sanitary facilities.

Laboratory rooms where flammable gases are produced must be equipped with fume hoods directly connected to air extraction systems.

- Emergency lighting, safety signs and escape plans

- Regular lighting (artificial or natural)

The regular lighting of interdepartmental corridors, hallways and stairways, must be provided 24 hours a day. This requirement does not apply when not all departments of the building are in operation.

The regular lighting of non interdepartmental corridors, hallways and stairways, must operate constantly during the operation of the relevant department they are a part of.

The minimum guaranteed light intensity in every part of the floor level must be set according to article 6 paragraph 4 of the General provisions.

- Emergency lighting

For Ε1, Ε2 and Ε3 buildings, the installation of emergency lighting on escape routes and emergency exits is obligatory.

The minimum light intensity in intensive care units, neonatal units and surgery and obstetrics complexes must be considered as high risk areas according to the ELOT Standard EN 1838.

For Ε3 buildings the power supply (main and auxiliary) of the lighting must come from reliable sources and the auxiliary power source must ensure as far as possible the operation of the emergency lighting even during a fire. The guaranteed duration of operation with an auxiliary power source must be at least 3 hours.

- Safety signs and escape plans

Escape routes, emergency exits and fire fighting equipment must be provided with safety signs.

Escape plans must be placed on the walls in the following cases:

a. In all buildings of class E3.

b. In all buildings of class Ε1 and Ε2 whose the main use covers three (3) or more storeys and whose theoretical population is over of two hundred (200) persons.

- Active fire protection means

- Portable fire extinguishers dry powder or water based

There must be one (1) fire extinguisher per 100 m2 of gross surface.

- Manual alarm system

A manual alarm system must be provided in the following cases:

a. In all buildings of class E1 and E3.

b. In all Ε2 buildings with a theoretical population of over 100 persons.

In addition to the positions imposed by ELOT EN 54, alarm devices shall be installed in the following positions:

- fire control panel;

- call centre;

- technical service;

- office of the person responsible for fire safety;

- nursing station;

- personnel areas.

In areas where there are patients or people with reduced mobility (i.e. medical care units), the alarm signal must be communicated only to personnel (i.e. pager, optical signs, etc.).

- Fire detection

An automatic fire detection system must be provided in the following cases:

a. In all buildings of class E1 and E3.

b. In all buildingsς of class Ε2 with three (3) or more storeys and/or with a theoretical population is over of two hundred (200) persons.

The fire detection - announcement system must have as an auxiliary power source a battery that must guarantee the system's operation for at least 30 hours.

- Permanent fire-fighting water supply network – simple fire-fighting water supply network

A permanent fire-fighting water supply network must be provided in the following cases:

a. For buildings classified in Ε1, Ε2 and Ε3 classes the height of which are more than 20 metres.

b. For buildings classified in Ε1, and Ε2 classes with four (4) or more storeys and a total surface of at least 3,000 m2.

c. For buildings classified in Ε1 and Ε2 classes with a total surface more than 5,000 m2, irrespective of the number of storeys.

d. Forbuildings classified in Ε3 class with more than 100 beds and if the floor level of their highest storey is higher than 12 metres above the floor of the evacuation storey.

Buildings used for health and social welfare purposes that are not obliged to have a permanent fire-fighting water supply network must have a simple fire-fighting water supply network (fire cabinet).

- Fire control panel

For buildings classified in Ε3 class a fire control panel (fire alarm annunciator panel) must be installed in a room that is always manned by personnel (such as a call centre or, preferably, a specific room where the control panel of the facility is installed).

The fire control panel must, according to the size of the complex, ensure the following operations:

Visual and audio alarm signal coming from a detection device (automatic or manual).

Transfer of the alarm signal to all alarm devices or to some of them (automatically or manually).

Group call of the fire protection group via a personnel call system (if required).

Possibility of placing an automatic call to the fire brigade.

Possibility of cooperation with the control panel of the facility to handle the facility, according to the action plan.

Status check of the facility (cables, appliances, etc.)

Occasional checks in combination with the control panel of the facility to ensure the safety of the building in case of fire (i.e. to release a door that is held by a mechanism, of interruption of supply in the provision of gas fuel, to check the ventilation facilities, etc.).

- Automatic fire extinguishing system

An automatic fire extinguishing system (water sprinkler) must be present in the following cases:

a. In basement areas of buildings classified in Ε3 class with a theoretical population of more than 150 persons. The automatic fire extinguishing system covers additionally the unprotected escape routes, up to each final emergency exit.

c. For buildings classified in Ε1 class with a total surface of more than 500 m2.

d. For buildings classified in Ε1 and Ε2 classes with a total height more that 23 metres.

## Article 6: Penitentiary

- General

This category includes buildings or parts of buildings that are used for detention, incarceration or serving of a sentence.

This category includes a.o. detention cells, youth detention centres and prisons.

- Design of escape routes

In case of controlled evacuation of the building during a fire, the area of temporary assemblage of inmates to which all escape routes lead, must be safe, outdoors and must have adequate surface to guarantee at least 2 m2 per person.

- Structural fire protection

Parts of buildings that contain the inmates' cells must be considered as separate fire compartments where it is forbidden to house other complementary uses that serve the penitentiary building.

Areas of risk, including central storage areas, car parking areas or the main kitchen, must be autonomous fire compartments with proper ventilation openings.

Boiler rooms and electromechanical facilities rooms must not be placed next to final exits.

Liquid fuel tanks must be placed outside the buildings and, preferably, they must be placed underground, according to the applicable specifications.

- Emergency lighting, safety signs and escape plans

It is mandatory and necessary to install security lighting on the escape routes of public areas and emergency exits.

Escape routes, emergency exits and fire fighting equipment must have safety signs.

- Preventive measures and necessary actions

The management and the responsible personnel of correctional facilities bear the responsibility for the prompt unlocking of the inmates' cells in case of fire.

- Active fire protection means

- Portable fire extinguishers dry powder or water based

There must be one (1) fire extinguisher per 150 m2 of gross surface.

- Fire detection

An automatic fire detection system and a manual fire announcement system must be present in all penitentiary buildings. The automatic fire detection system may not cover detainees’ booths, if deemed appropriate by the competent Directorate of the Ministry of Justice, Transparency and Human Rights.

Sound alarm devices must be placed in the following areas:

  - call centre;

  - reception kiosks

  - areas of staff accommodation

  - offices of supervisors and fire safety officers.

- Permanent fire-fighting water supply network – simple fire-fighting water supply network

A permanent fire-fighting water supply network must be installed in correctional facilities with a population of more than 150 persons and in buildings higher than 15 metres.

Penitentiary buildings not obliged to have a permanent fire-fighting water supply network must have a simple fire-fighting water supply network (fire cabinet).

- Automatic fire extinguishing systems

An automatic fire extinguishing system (water sprinkler) must be present in the following cases:

a. In penitentiary buildings with a total covered surface of at least 3,500 m2, irrespective of the number of storeys.

b. In underground detention areas with a total covered surface of more than 500 m2.

The automatic fire-fighting system may not cover detainees’ booths, if deemed appropriate by the competent Directorate of the Ministry of Justice, Transparency and Human Rights.

## Article 7: Commerce

- General

This category includes buildings or parts of buildings intended for the exhibition, sale and storage of goods, such as stores selling goods for personal or home use or consumption, department stores (that have a vast array of goods, including among others clothes, furniture, home appliances, cosmetics, jewellery, toys, sports goods, etc.), shopping malls, marketplaces and supermarkets, hair salons, establishments of sanitary interest for people standing or passing by or equipped with benches and stools.

Indicative complementary uses in this category are a small warehouse, a small restaurant, a small playground, a canteen, a kitchen, locker rooms, etc.

If there is a storage area inside in a store that is used exclusively by it, and this storage area is not a high risk room (category Ζ3 according to article 10) and has a total surface of up to 250 m2, without being larger than the surface of the shop, then the storage room is considered as a complementary use of the shop and this area falls under the scope of this article.

High-risk shops are those marketing paints, varnishes and other chemicals, hunting and explosives, guns and munitions – Bengali, insulating materials, fertilisers and agrochemicals.

- Calculating the theoretical population

In addition to the general provisions concerning the calculation of the population in the areas intended for circulation in buildings used for commerce, where there is a covered patio, the following apply:

a. For areas intended for the circulation of people with a gross surface of up to 14,000 m2, the theoretical population factor is set to 2.8 m2/person.

b. For a gross surface of more than 14,000 m2, the factor is set to 3.3 m2/person. This factor is increased by 0.1 m2/person for every 1,000 m2 or a fraction of that over 14,000 m2.

The used areas that are served by the above mentioned circulation areas of the covered patio must be provided with independent emergency exits and for the design purposes, they must be considered as parts of the escape routes.

- Design of escape routes

In case the shop is characterised as high risk due to the nature of its products, i.e. there is a high risk of fire and/or its products are highly flammable, can cause rapid surface flame spread, heat release, produce toxic fumes and/or entail a risk of explosion, the shop must:

a) have separate escape routes than the rest of the building;

b) be a separate fire compartment.

The aisles used for circulation between goods inside the areas of the shops, which must be indicated in the plans of the fire protection analysis, must be at least 0.70 metres wide. At least one of these aisles must be 1.20 metres wide and lead directly to an emergency exit.

In addition to the general provisions, the number and width of the emergency exits in every storey are set according to the following table:

| Number and width of emergency exits per storey |  |  |
| --- | --- | --- |
| Theoretical population | Minimum number of exits | Minimum width of all exits |
| Up to 50 | 1* | 0.90 metres |
| 51 - 150 persons | 2 | 0.90 metres |
| 151 - 300 persons | 2 | 1.40 metres |
| 301 - 500 persons | 3 | 1.60 metres |
| 501 - 800 persons | 4 | 1.80 metres |

* By way of exception, in underground main use areas, there must be at least two (2) emergency exits with a minimum width of 0.90 metres.

For a population of over 800 persons, there must be one additional emergency exit that is 1.80 metres wide for every 400 persons or a fraction of that.

In order not to hinder mass escape, there must be alternative routes leading to final exits whose width is of at least equal to 40% of the total required width; these routes must not pass through control areas (shop tills).

An exception for the pyramidalisation of buildings of category thereof it is possible for up to 25 % of the internal wall surface of fire compartment boundaries to use fire resistant rolls or firecurtains of equivalent integrity and thermal insulation capacity interconnected with the fire detection system, closed at less than 1 min. These elements must not affect the design of escape routes and must, additionally, have an auxiliary power source.

- Emergency lighting, safety signs and escape plans

Emergency lighting must be installed on all escape routes and emergency exits.

Escape routes, emergency exits and fire fighting equipment must be provided with safety signs.

Escape diagrams must be placed:

- in areas and buildings used for commercial purposes whose main use covers three (3) or more storeys

- in areas and buildings used for commercial purposes with a theoretical population of over 300 persons.

- Active fire protection means

- Portable fire extinguishers dry powder or water based

There must be one (1) fire extinguisher per 150 m2 of gross surface.

In highly risk stores, there must be one (1) fire extinguisher per 100 m2 of gross surface.

- Manual alarm system

A manual alarm system must be provided in the following cases:

a. In shops whose total surface is at least 500 m2.

b. In high risk shops.

- Fire detection

An automatic fire detection system must be provided in the following cases:

a. in areas and buildings used for commercial purposes with three (3) or more storeys;

b. in areas and buildings used for commercial purposes with a total covered area of more than 1,000 m2;

c. In stores with a high degree of risk.

d. In covered patios. The activation of the automatic fire detection system must, additionally, lead to the activation of the mechanical ventilation system and preferably to the rapid opening of at least 50% of the surface of the patio's roof (in under 1 minute).

- Permanent fire-fighting water supply network – simple fire-fighting water supply network

A permanent fire-fighting water supply network must be provided in the following cases:

a. in areas and buildings used for commercial purposes with a total covered area of at least 2,000 m2;

b. in high risk areas and buildings used for commercial purposes, whose total covered area is at least 1,000 m2;

Buildings or areas used for commercial purposes not obliged to have a permanent ire-fighting water supply network must have a simple ire-fighting water supply network .

- Automatic fire extinguishing systems

An automatic fire extinguishing system (water sprinkler) must be present in the following cases:

a. in areas and buildings used for commercial purposes with a total covered area of at least 2,500 m2;

b. in high risk areas and buildings used for commercial purposes, whose total covered area is at least 250 m2;

c. in all multi-storey buildings used for commercial purposes with a storey surface of more than 1,000 m2;

d. in all underground areas with a surface larger than 250 m2.

## Article 8: Offices

- General

The provisions of this article apply to buildings housing businesses facilities used for intellectual, managerial activities or for the provision of services, if they are not included in the category of commerce, such as public service or company offices.

Indicative complementary uses in this category are small warehouses, kitchens, restaurants serving exclusively the personnel of said offices, small meeting rooms, archive rooms, libraries, etc.

- Design of escape routes

The minimum width of the escape route is set to 0.90 metres.

In addition to the general provisions, the number and width of the emergency exits in every storey are set according to the following table:

| Number and width of emergency exits per storey |  |  |
| --- | --- | --- |
| Theoretical population | Minimum number of exits | Minimum width of all exits |
| Up to 50 | 1* | 0.90 metres |
| 51 - 150 persons | 2 | 1.10 metres |
| 151 - 400 persons | 2 | 1.40 metres |
| 401 - 700 persons | 3 | 1.60 metres |
| 701 - 1000 persons | 4 | 1.80 metres |

*By way of exception, in underground main use areas, there must be at least two (2) emergency exits with a minimum width of 0.90 metres.

For a population of more than 1000 persons, there must be one additional exit that is 1.80 metres wide for every 250 persons or a fraction of that.

- Emergency lighting, safety signs and escape plans

Emergency lighting must be installed on all escape routes and emergency exits.

Escape routes, emergency exits and fire fighting equipment must be provided with safety signs.

Escape diagrams must be placed on the walls in offices whose main use covers three or more storeys, as well as in offices with a theoretical population of more than 200 persons.

- Active fire protection means

- Portable fire extinguishers dry powder or water based

There must be one (1) fire extinguisher per 150 m2 of gross surface.

- Manual alarm system

A manual alarm system must be installed in offices with a theoretical population of more than 100 persons.

- Fire detection

An automatic fire detection system must be provided in the following cases:

a. In offices with a theoretical population of more than 200 persons.

b. In offices with three (3) or more main use storeys.

- Permanent fire-fighting water supply network – simple fire-fighting water supply network

A permanent fire-fighting water supply network must be provided in the following cases:

a. In offices with four (4) or more storeys and a total surface of at least 3,000 m2.

b. In offices with a total surface of at least 5,000 m2, irrespective of the number of storeys.

c. In office buildings taller than 20 metres.

Offices not obliged to have a permanent fire-fighting water supply network must have a simple fire-fighting water supply network (fire cabinet).

- Automatic fire extinguishing systems

An automatic water-based fire extinguishing system (water sprinklers) must be installed in office buildings taller than 23 metres.

## Article 9: Industry - Small crafts industry

- General

This category includes buildings or parts of buildings housing industries, small craft industries, workshops, preparation areas where several products are produced or manufactured, as well as industrial warehouses, containing electromechanical equipment.

Industries and small crafts industries are classified in three (3) subcategories, depending on the risk of causing a fire to start, according to the Annex to the Joint Ministerial Decision 1589/104/2006 (B’ 90), in its current version:

Ζ1: low risk 	(Ο, Aa, Ba, Ca, D)

Ζ2: medium risk 	(Ab, Bb, Cb)

Ζ3: high risk 	(Ac, Bc, Cc)

Indicative complementary uses in this category are small offices, small shops, small warehouses and small public assemblage areas, etc.

- Design of escape routes

The minimum width of escape routes is set to 1.00 metre, whereas the minimum unobstructed width for the doors to the escape routes is 0.85 metres and for sanitary facilities 0.75 metres.

In addition to the general provisions, the number and width of the emergency exits in every storey are set according to the following table:

| Number and width of emergency exits per storey |  |  |
| --- | --- | --- |
| Theoretical population | Minimum number of exits | Minimum width of all exits |
| Up to 30 | 1* | 0.90 metres |
| 31 - 150 persons | 2 | 1.10 metres |
| 151 - 400 persons | 2 | 1.40 metres |
| 401 - 700 persons | 3 | 1.60 metres |
| 701 - 1000 persons | 4 | 1.80 metres |

*By way of exception, in underground main use areas, there must be at least two (2) emergency exits with a minimum width of 0.90 metres.

For a population of more than 1000 persons, there must be one additional exit that is 1.80 metres wide for every 250 persons or a fraction of that.

Vertical stairs (ladders) serving the level of mechanical facilities may be parts of the escape routes, if they do not serve more than 3 persons.

- Structural fire protection

Corridors longer than 40 metres must be interrupted by doors with a degree of fire resistance equal to 30 minutes, and they must be self-closing in order to protect from the spreading of fire and smoke.

The maximum volume of fire compartments is presented in the following table:

| Maximum volume of fire compartments (in m3) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Category of industrial building | Single-storey | Multi-storey | Basements | Scaling factor due to the presence of an automatic water extinguishing system (water sprinkler) (*) |
| Ζ1 | 60,000 | 18,000 | 8,000 | 2 |
| Ζ2 | 30,000 | 12,000 | 5,000 | 2 |
| Ζ3 | 24,000 | 9,000 | 4,000 | 2 |

* Volume scaling factor in case there is an automatic water-based fire extinguishing system (water sprinkler) in the fire compartment.

By way of exception, for the fire compartmentingν of main use areas of industry-small crafts industry buildings that fall under the Ζ1 or Ζ2 category, it is possible to use in up to 25% of the surface that must be separated in fire compartments, instead of fixed building elements, fire resistant roller shutters or fire curtains of the same integrity and thermal insulation capacity, which must be connected to the fire detection system and close in less than 1 minute. These elements must not affect the design of escape routes and must, additionally, have an auxiliary electrical power source.

- Emergency lighting, safety signs and escape plans

Emergency lighting must be installed on all escape routes and emergency exits.

Emergency lighting must be installed on routes up to the final emergency exit, in cases where the industry-small crafts industry is on a storey.

Escape routes, emergency exits and fire fighting equipment must be provided with safety signs.

Escape diagrams must be placed on the walls in industries with three (3) or more storeys, as well as in industries with a total theoretical population of over 50 persons.

- Active fire protection means

- Portable fire extinguishers dry powder or water based

There must be at least one (1) fire extinguisher installed for every 250, 200 and 150 m2 of gross surface in Ζ1, Ζ2 and Ζ3 industries-small craft industries, respectively.

- Manual alarm system

A manual alarm system must be provided in the following cases:

a. In multi-storey industry - small crafts industry buildings with storey surface over 1,000 m2.

b. In industries-small crafts industries with a total covered surface of more than 2,500 m2.

The system must emit a signal in an area that is always manned by service personnel.

- Fire detection

An automatic fire detection system must be provided in the following cases:

a) in all Z3 industries – small crafts industries;

b) in all Z2 industries - small crafts industries with a total covered surface of over 2,000 m2.

- Permanent fire-fighting water supply network – simple fire-fighting water supply network

A permanent fire-fighting water supply network must be provided in the following cases:

a. in industries - small crafts industries with a total surface of over 2,500 m2;

b. in Z3 industries - small crafts industries with a total covered surface of at least 1,000 m2;

c. in multi-storey industry-small crafts industry buildings that cover more than three (3) storeys and where the surface of at least one storey is more than 1,000 m2.

Industries-small crafts industries not obliged to have a permanent fire-fighting water supply network must have a simple fire-fighting water supply network.

- Automatic fire extinguishing systems

An automatic fire extinguishing system using water or other suitable fire extinguishing material must be placed in all Z3 industries-small craft industries with a total surface over 2,000 m2.

Article 10: Storage

- General

This category includes buildings or parts of buildings that are used for the storage of goods, the safekeeping of objects or the housing of animals, such as general commercial warehouses, storage and distribution centres (logistics centres), agricultural warehouses, etc.

Warehouses are classified in three (3) subcategories, depending on the risk of causing a fire to start, according to the Annex to the Joint Ministerial Decision 1589/104/2006 (B’ 90), in its current version:

Ζ1: low risk 	(Ο, Aa, Ba, Ca, D)

Ζ2: medium risk 	(Ab, Bb, Cb)

Ζ3: high risk 	(Ac, Bc, Cc)

For example, category Ζ1 includes areas intended for the storage of food and non-alcoholic drinks, metal products and electric appliances.

Category Z2 includes indicatively the Storage and Distribution Centers (logistics), the warehouses of supermarkets, the warehouses of paper, textiles, footwear, clothes, fertilizers and pesticides.

Category Ζ3 includes, inter alia, warehouses for the storage of foam or monomeric plastic and nitrocellulose.

A more detailed classification as to the category of risk is performed using the mean density of the fire load and is obligatory in case that load remains relatively stable, according to the following pattern:

| Ζ1: | fire load | < 1000 | MJ / m2 |
| --- | --- | --- | --- |
| Ζ2: | fire load | 1000 - 2000 | MJ / m2 |
| Ζ3: | fire load | >2000 | MJ / m2 |

Indicative complementary uses in this category are small offices, small shops, etc.

- Design of escape routes

The minimum width of escape routes is set to 1.00 metre, whereas the minimum unobstructed width for the doors to the escape routes is 0.85 metres and for sanitary facilities 0.75 metres.

In addition to the general provisions, the number and width of the emergency exits in every storey are set according to the following table:

| Number and width of emergency exits per storey |  |  |
| --- | --- | --- |
| Theoretical population | Minimum number of exits | Minimum width of all exits |
| Up to 30 | 1* | 0.90 metres |
| 31 - 150 persons | 2 | 1.10 metres |
| 151 - 400 persons | 2 | 1.40 metres |
| 401 - 700 persons | 3 | 1.60 metres |
| 701 - 1000 persons | 4 | 1.80 metres |

*By way of exception, in underground main use areas, there must be at least two (2) emergency exits with a minimum width of 0.90 metres.

For a population of more than 1000 persons, there must be one additional exit that is 1.80 metres wide for every 250 persons or a fraction of that.

Vertical stairs (ladders) serving the level of mechanical facilities may be parts of the escape routes, if they do not serve more than 3 persons.

- Structural fire protection

Corridors longer than 40 metres must be interrupted by doors with a degree of fire resistance equal to 30 minutes, and they must be self-closing in order to protect from the spreading of fire and smoke.

The maximum volume of fire compartments is presented in the following table:

| Maximum volume of fire compartments (in m3) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Category of industrial building | Single-storey | Multi-storey | Basements | Scaling factor due to the presence of an automatic water extinguishing system (water sprinkler) (*) |
| Ζ1 | 60,000 | 12,000 | 4,000 | 2 |
| Ζ2 | 40,000 | 9,000 | 3,000 | 2 |
| Ζ3 | 24,000 | 6,000 | 2,000 | 2 |

* Volume scaling factor in case there is an automatic water-based fire extinguishing system (water sprinkler) installed in the fire compartment.

By way of exception, for the fire compartmenting of main use areas of warehouses that fall under the Ζ1 or Ζ2 category, it is possible to use in up to 25% of the interior wall area of fire compartment boundaries instead of fixed structural building elements, fire resistant roller shutters or fire curtains of the same integrity and thermal insulation capacity, which must be connected to the fire detection system and close in less than 1 minute. These elements must not affect the design of escape routes and must, additionally, have an auxiliary power source.

- Emergency lighting, safety signs and escape plans

Emergency lighting must be installed on all escape routes and emergency exits.

Emergency lighting must be installed on routes up to the final emergency exit, in cases where the warehouse is on a storey.

Escape routes, emergency exits and fire fighting equipment must be provided with safety signs.

Escape diagrams must be placed on the walls in warehouses with three (3) or more storeys, as well as in warehouses with a total theoretical population of over 50 persons.

- Active fire protection means

- Portable fire extinguishers dry powder or water based

There must be at least one (1) fire extinguisher installed for every 250, 200 and 150 m2 of gross surface in Ζ1, Ζ2 and Ζ3 warehouses, respectively.

- Manual alarm system - Fire detection

A manual alarm system and an automatic fire detection system must be installed in the following cases:

a. Warehouses with a total covered surface area of more than 1,000 m2.

b. Z3 warehouses.

c. Warehouses that take up 3 or more storeys.

- Permanent fire-fighting water supply network – simple fire-fighting water supply network

- A permanent fire-fighting water supply network must be provided in the following cases:

a. in warehouses with a total covered surface area of at least 2,000 m2;

b. in Z3 warehouses with a total covered surface area of at least 1,000 m2;

c. in multi-storey warehouses including three (3) or more storeys with at least one storey's surface being over 500 m2.

Warehouses not obliged to have a permanent fire-fighting water supply network must have a simple fire-fighting water supply network.

- In case the goods are stored in open or semi-open areas of buildings or plots, provisions must be made for a permanent fire-fighting water supply network as follows:

a. Category Ζ1 storage, with a total storage surface area of over 5,000 m2.

b. Category Z2 storage, with a total storage surface area of over 4,000 m2.

c. Category Z3 storage, with a total storage surface area of over 3,000 m2.

Warehouses in open or semi-open areas of buildings or plots that are not obliged to have a permanent fire-fighting water supply network must have water abstraction points with fixed elastic water hoses equipped with a nozzle that cover all areas. These hoses must be placed in suitable spots inside special cabinets. In case there is no water supply network in the area, it is not necessary to meet this requirement, however there must be at least one (1) portable dry powder fire extinguisher per each surface of 500 sq.m.

- Automatic fire extinguishing systems

An automatic extinguishing system using water or other suitable material must be installed in the following cases:

a. in Z2 warehouses, if their total surface is more than 2,000 m2;

b. in Z3 warehouses.

## Article 11: Parking areas & petrol stations

- General

This category includes buildings or parts of buildings used for the service of vehicles, such as parking areas, fuel and gas energy stations, car washes, etc.

They are classified in four sub-categories:

L1: Ground level parking areas.

L2: Above ground level parking areas.

L3: Below ground level parking areas.

L4: Petrol stations, car-washes, spaces with fuel pumps in private enterprises and other such uses in stations.

Additionally, parking buildings are divided in open and closed buildings, depending on whether there are gaps in the masonry surrounding the parking area, that are left open without any frames.

In case a building of any use contains one or more parking areas with a capacity of up to ten (10) spaces, each one must be an independent fire compartment. In this case, the requirements of this article must be met only as far as the active fire protection means are concerned. In all other cases, the area is considered ancillary to the main use.

In the case of a parking space for vehicles with a capacity of more than 10 seats, this must also be a separate fire compartment and the provisions of this article apply to this space. The provisions of article 4, par. 4.2.2, subparagraph iii of Chapter A on mixed uses do not apply for this category of buildings.

- Theoretical population

To calculate the theoretical population of class L4 buildings or parts of buildings, we use a ratio of one person per 6 m2.

The theoretical population of waiting rooms and tills in parking areas using mechanical means is based on a ratio of 0.5 persons per stationed vehicle. For the remaining areas, where vehicles park, care must be taken for the escape of 1-3 persons (supervision and maintenance staff).

- Design of escape routes

There must be at least two emergency exits from every point of the storeys of buildings belonging to this category.

- In buildings or parts of buildings used for parking (L1, L2, L3) a ramp intended for the movement of vehicles may be used as a second alternative escape route if:

a) it serves only one parking storey, or one evacuation storey-exit in case of a parking controlled by mechanical means;

b) the side of the ramp that is towards the parking area consists of a fire resistant construction with a degree of fire resistance of at least 60 minutes;

c) there is a pedestrian crossing on the ramp.

In any case, when the second escape route passes through the ramp, there must be a provision for a permanent opening or door for the direct exit of the population from the parking area.

- In case a parking building is equipped with liquid fuel pumps, then the level on which the pumps are located is a separate fire compartment with a degree of fire resistance of 120 minutes and during the design of the escape routes, care must be taken in order to guarantee at least two unobstructed emergency exits, in case of fire or explosion of a pump.

- For parking areas using mechanical means, the above mentioned applies only to the evacuation storey (vehicle exit, tills, etc.). In K4 category buildings, the second emergency exit must not be located close to the side where the characteristic parts of a petrol station are (such as pumps, tanks, tank venting system, spaces intended for the tank filling vehicles, etc.), whereas care must be taken so that in case of fire the route, after exiting the building until reaching the common road, is not obstructed by facilities, parked cars, etc. This route must be at a distance of at least 2 metres from these characteristic parts.

- In parking areas of more than 100 parking spaces, there must be spaces especially marked next to the outer walls, for cars using gas fuel. These must be at least 10% of the total parking spaces. These parts must be a separate fire compartment, they must be placed preferably in above-ground storeys and have a suitable ventilation system.

- For buildings classified inL4 class which are used as car wash that are not in the same area as petrol stations, it is allowed to have only one (1) emergency exit.

When petrol stations are also used for other uses (i.e. cafés, shops, car wash, etc.), then these uses must be separate fire compartments and meet the minimum requirements for buildings classified in class L4.

- Structural fire protection

Internal stairways in multi-storey car parking areas must be fire protected.

In parking areas using mechanical means, irrespective of the number of storeys, the internal stairways must be fire protected, have fire resistant self-closing doors, a minimum degree of fire resistance of at least 60 minutes and they are additionally required to have a special fire protected hallway.

In closed above ground parking areas, there must be ventilation openings with a surface at least equal to 5% of the surface area of each storey. Equivalent natural or artificial ventilation must also be ensured for underground parking areas. The openings of entrance-exit ramps that are located on the walls of the area are added to the ventilation openings. Especially for underground parking areas using mechanical means for the parking of vehicles, in case it is not possible to have natural ventilation, there must be mechanical ventilation renewing the air 6 times per hour (under normal circumstances) and ten times per hour in case of fire.

In case of multi-storey parking buildings (vehicle stations) where the ramp or ramps must be interrupted via a fire resistant door, in order to separate the fire compartments per storey, this door must close automatically upon activation of the fire detection and alarm system.

The buildings od class L4 ε located into petrol stations areas must guarantee a minimum degree of fire resistance equal to 120 min. Any basements in these buildings must be separate fire compartments with a degree of fire resistance equal to 120 minutes and at least two emergency exits.

The minimum requirements on the external walls:

a. in buildings of class L4 located inside petrol stations

b. of buildings adjacent to petrol stations,

as far as the characteristic parts of the station are concerned, are set in the following table:

Requirements on the control of external fire spread in buildings used as petrol stations

| Building element | Distance the wall of a building L4 from characteristic parts |  |  |  |
| --- | --- | --- | --- | --- |
|  | < 2 m. | 2-5 m. | 5-10 m. | > 10 m. |
| a) degree of fire resistance of external wall | 120 min | 120 min | 60 min | 30 min |
| b) external coating | Α2-s1, d0 | A2-s1, d1 | B-s1, d2 | C-s1,d2 |
| c) percentage of openings | 0% | 20% | 50% | 80% |

An exception for the pyrodisation of buildings of category L1 , L2 and L3 it is possible for up to 50 % of the internal wall surface of fire compartment boundaries instead of fixed building elements to use fire resistant rolls or firecurtains of equivalent integrity and thermal insulation capacity interconnected with the fire detection system, closed at less than 1 min. These elements must not affect the design of escape routes and must, additionally, have an auxiliary power source.

- Emergency lighting, safety signs and escape plans

Emergency lighting must be installed on all escape routes and emergency exits.

Escape routes, emergency exits and fire fighting equipment must have safety signs.

Escape diagrams must be placed on the walls in parking areas of three or more storeys, as well as in parking areas with a total surface of more than 1,000 m2.

- Preventive measures – necessary actions

In parking areas with less than 100 parking spaces, it is recommended to have spaces especially marked next to the outer walls, for cars using gas fuel.

- Forbidden activities

In addition to the special safety provisions for facilities of this category, as defined in the relevant applicable laws, the following actions-activities are forbidden:

- Smoking and use of flame producing devices.

- The outdoor assemblage of people and the placement of tables and chairs at a distance of less that 10 metres from the characteristic parts of petrol stations.

- Parking of cars (not temporary stop) in outdoor areas of petrol stations at a distance of less that 10 metres from the characteristic parts.

- Active fire protection means

  - Portable fire extinguishers dry powder or water based – wheeled fire extinguishers

In parking buildings there must be at least one (1) portable fire extinguisher per five parking spaces for cars or eight parking spaces for two-wheel vehicles.

These requirements must also be met in case the number of parking spaces is less than ten.

Fire extinguishers must be placed in such a way, that no part of the protected area is further than 15 m. away from the nearest fire extinguisher.

It is necessary to install one (1) wheeled fire extinguisher on each floor.

There must also be a bucket full of sand, with a capacity of at least 25 kg, and a shovel on every storey.

- Manual alarm system - automatic fire detection system - automatic flammable gas detection system

There must be an automatic fire detection and a manual fire announcement system in all car stations with a surface of more than 250 m2.

In vehicle stations with more than 100 spaces there must be an automatic flammable gas detection system that covers every parking space that is intended for vehicles using gas fuel.

In buildings of class L4 that are inside petrol stations, excluding parts housing car washes, there must be an automatic fire detection system and a manual fire announcement system.

- Permanent fire-fighting water supply network – simple fire-fighting water supply network

A permanent fire-fighting water supply network must be present in buildings of class L2 with a height taller than 15 metres, as well as on all buildings of class L3.

Parking areas not obliged to have a permanent fire-fighting water supply network must have a simple fire-fighting water supply network (fire cabinet).

Parking areas with less than 10 spaces, must be equipped with a simple fire-fighting water supply network (fire cabinet).

- Automatic fire extinguishing systems

An automatic water-based fire extinguishing system (water sprinklers) must be installed in the following cases:

a. In all underground parking spaces, the total area exceeds 500 m².

b. For buildings classified in L4 class that are located inside petrol stations with a surface more than 300 m2. In that case, the area covered by a car wash is not calculated and it is not required to install a fire fighting system in that part.

# CHAPTER C:

## Article 1: Repealed provisions - Authorisations

## Article 2: Transitional provisions

## Article 3: Entry into force

## Article 1: Repealed provisions - Authorisations

- The entry into force of this Regulation repeals Chapters A and C of Presidential Decree 71/1988 (Α΄ 32).

- Chapter B "Regulation on the Fire Protection of Existing Hotels" of Presidential Decree 71/1988 (A’ 32) remains in force until the adoption of the Regulation on the Fire Protection of Existing Buildings.

- The Committee responsible for the Authorisation of Fire Protection Analyses which has been set up by the number 26539/17-06-2015 Joint Ministerial Decision (Β’ 1373) under the authority of paragraph 5 of article 15 of the Presidential Decree 71/1988 (A' 32), as added by the Ministerial Decision. 33940/750/31-12-1998 (B’ 1316), remains in force until the end of its mandate and is replaced by the committee mentioned in article 2 paragraph 2.5 of the Chapter A of the present Regulation.

## Article 2: Transitional provisions

## In case of applications submitted for the issue of building permits for buildings, which have been considered according to the provisions of Presidential Decree 71/88, the provisions of article 26 of law 2831/2000 (A '140), as it is in force, shall apply.

## Article 3: Sanctions

Failure to apply the provisions of this Regulation shall give rise to the penalties laid down by law.

## Article 4: Annexes

Annexes A, B, C, D are hereby annexed and form an integral part thereof, as follows:

ANNEXES

ANNEX A

CLASSIFICATION OF BUILDINGS ACCORDING TO THEIR USE UNDER THE BUILDING REGULATION

| USE CATEGORIES |  | DESCRIPTION |
| --- | --- | --- |
| A | RESIDENCE | buildings of three or more apartments, detached houses, semi-detached houses, shared houses |
| B | TEMPORARY ACCOMODATION | hotels, hostels, boarding institutions and dormitories for persons > 6 years old |
| C | PUBLIC ASSEMBLAGE | assemblage of at least 50 persons, conference rooms, large teaching rooms, exhibition areas, museums, concert halls, court rooms, temples, sports events areas, theatres, cinemas, restaurants, pastry shops, cafés, entertainment halls, multi-use halls, passenger waiting areas, tables ≥ 70 m2 |
| D | EDUCATION | teaching of 6-49 persons, compulsory education buildings, private tuition centres, kindergartens |
| E | HEALTH AND SOCIAL WELFARE | buildings intended for preventive, diagnostic and treatment purposes, for providing sleep and physical hygiene of infants, such as hospitals, clinics, regional medical practices, health stations, health centres, mental health clinics, facilities for people with disabilities, facilities for people suffering from chronic diseases, homes for the elderly, crèches <5* years, nurseries, medical practices |
| F | PENITENTIARY | buildings intended for detention, incarceration or serving of a sentence, detention cells, youth detention centres, prisons |
| G | COMMERCE | shopping malls, markets and supermarkets, shops, pharmacies, barbershops, hairdressers, fitness institutes, small clothing and footwear repair shops |
| H | OFFICES | public service offices, local government offices, libraries, business offices, freelancer offices, banks of a gross surface < 70 m2 |
| Ι | INDUSTRY - SMALL CRAFTS INDUSTRY | industries, small crafts industries, workshops, preparation areas, services with electromechanical equipment such as factories, oil refineries, energy production stations, car repair shops, dyeing workshops, carpenter's workshops, laboratories for research and educational purposes, food preparation areas, dry cleaning services, ironing services, laundry services, autonomous computer centres |
| J | STORAGE | general storage rooms, agricultural storage rooms, harbour depots, museum warehouses, shop storage rooms, stables, ox-stalls, pig-stalls, chicken rearing facilities |
| K | PARKING SPACE AND PETROL STATIONS | buildings intended for the parking of two-, three- and four-wheel vehicles or petrol stations and energy suppliers** or car washing stations |

*THE MINISTERIAL DECISION 3046/89 refers to children under the age of 6 and now compulsory education starts at the age of 5 years old.

**In Ministerial Decision Reference of the 3046/89 is made only in respect of service stations for liquid fuels, but now all fuel and power stations belong to this category.

ANNEX Β

Treatment of single- or multi-use buildings in terms of fire protection

| KTIPIO | BUILDING |
| --- | --- |
| Μία χρήση | Single use |
| Κύρια με συμπληρωματικές | Main use with complementary uses |
| Κύρια και μοναδική | Only main use |
| Η συμπληρωματική χρήση διαθέτει πληρότητα | The complementary use is fully used |
| Η συμπληρωματική χρήση δε διαθέτει πληρότητα | The complementary use is not fully used |
| Διαθέτει πληρότητα | Fully used |
| Δε διαθέτει πληρότητα | Not fully used |
| Εξετάζεται κάθε χρήση με тο ειδικό άρθροτης | Each use is considered based on its respective article |
| Εξετάζεται συνολικά με την κυριαρχούσα χρήση | Considered in combination with the predominant use |
| Εξετάζεται με тο ειδικό άρθροτης χρήσης | Considered based on its respective article |
| Εξετάζεται με τη συγγενέοτερη χρήση | Considered in combination with the most relevant use |
| Εάν η συμπληρωματική χρήση δεν διαθέτει ανεξάρτητες οδεύσεις | If the complementary use has no independent routes |
| Ο θεωρητικός πληθυσμός (Θ.Π.) της συμπληρωματικής προσμετράται στο Θ.Π. της κυριαρχούσας | The theoretical population (T.P.) of the complementary use is added to the T.P. of the predominant use |
| Πολλαπλών χρήσεων | Multi-use |
| Εμπλεκόμενες | Mixed |
| Διαχωρισμένες (Πυράντοχος διαχωρισμός και ανεξάρτητες οδεύσεις διαФυγής) | Separate (Fire resistant separation and independent escape routes) |
| Χρήσειςπου διαθέτουν πληρότητα | Uses are fully used |
| Χρήση δεν διαθέτει πληρότητα | Use is not fully used |
| Εξετάζεται κάθε χρηση με το ειδικό άρθρο της για το σύνολο του κτιρίου | Each use is considered based on its specific article for the whole building |
| Επιλέγονται οι κατά περίπτωση αυστηρότερες απαιτήσεις της κάθε χρήσης για το σύνολο του κτιρίου | The strictest requirements for each use are chosen for the whole building |
| Εξετάζεται με την κυριαρχούσα χρήση, ως δευτερεύουσα | Considered in combination with the predominant use, as ancillary use |
| Εάν υπάρχει πυράντοχος διαχωρισμός και οι χρήσεις είναι τμήματα διαФορετικών ορόФων με κοινές πυροπροστατευμένες κατακόρυФες οδεύσεις | If there is fire resistant separation and the uses are parts of different storeys with common fire protected vertical routes |
| Εξετάζεται κάθε χρήση ξεχωριστά, μόνο για την επιβολή των μέσων ενεργητικής πυροπροστασίας | Each use is considered separately only as far as the enforcement of active fire protection means is concerned |

## ANNEX C

## Fire resistance - degree of fire resistance

The degree of fire resistance of a building element is defined through laboratory fire resistance tests, according to standard ELOT EN 13501-2. The degree of fire resistance corresponds to the time frame during which a building element, when subject to a predetermined thermal and mechanical load, meets specific thermal and mechanical reaction criteria. The most important evaluation criteria, that are used to determine the respective degrees of fire resistance are shown in Table C.1.

Table C.1: Indicative evaluation criteria for the determination of the degree of fire resistance

| Symbol | Criterion | Description |
| --- | --- | --- |
| R | Load bearing capacity(load bearing capacity) | The capacity of a load bearing building element to withstand mechanical actions, while exposed to fire on one or more sides, without losing its structural load bearing capacity. |
| E | Integrity(integrity) | The capacity of a separating building element, when exposed to fire on one side, to block flames, hot gas and smoke, hindering them from reaching its non exposed side. |
| I | Thermal insulation(thermal insulation) | The capacity of a separating building element, when exposed to fire on one side, to limit the increase of heat on its non exposed side within predetermined limits. |
| W | Limitation of radiation(limitation of radiation) | The capacity of a building element when exposed to fire on one side to limit the possibility ofς thermal radiation transfer, either through the element itself, or through its non exposed side to adjacent materials. |
| M | Mechanical resistance(mechanical resistance) | The capacity of a building element to withstand the effect of a predetermined impact force due to a building failure of another element. |
| C | Self closure(self closure) | The capacity of building elements (doors or roller shutters) to close fully and automatically without human interference, irrespective of whether there is a power supply. |
| S | Smoke leakage(smoke leakage) | The capacity of a building element to reduce or limit hot gases or smoke passing from its one side to the other. |

Resistance to fire is an essential characteristic of construction products directly related to the second essential requirement for ‘fire safety’ construction works set out in Annex I to Regulation (EU) No 305/2011 and is provided for by the manufacturer as a class of performance (euroclasses) in the declaration of performance referred to in Article 6 of that Regulation.

The degree of fire resistance of a building element is expressed with a combination of symbols in the form "XX tt". The first part (XX) of the fire resistance indicator corresponds to the symbolism of the fire resistance criterion required in each case (see Table B.1), while the second part (tt) corresponds to the maximum time (in minutes) for

which the relevant criterion is met accordingly. Time is selected from a list of standard duration categories (15, 30, 45, 60, 90, 120, 180, 240, 360) and corresponds to the maximum time during which the relevant criterion is met according to the measurements of the laboratory test. In case there is a combined requirement for two or more fire resistance criteria, the respective degree of fire resistance is determined as the minimum time frame during which both criteria are met. For example, a building element that, according to the standard fire resistance test has a load bearing capacity of 155 minutes, integrity of 80 minutes and thermal insulation capacity of 42 minutes, may be classified as to its degree of fire resistance in category R 120 or RE 60 or REI 30.

The harmonised Euroclass system is based, as far as fire resistance is concerned, on the proper use of standard laboratory tests, as described in Table C.2.

It is also equally acceptable for any other laboratory test used in any EU Member State or in Turkey or in a EFTA State party to the EEA Agreement is also accepted, if it can be proven to guarantee an equivalent level of quality and safety.

Table C.2 Standard fire resistance tests for the determination of the degree of fire resistance.

| GENERAL INFORMATION |  |
| --- | --- |
| EN 1363 -1 | Fire resistance tests, General requirements |
| EN 1363 -2 | Alternative and additional procedures |
| EN 1363 -3 | Verification of furnace performance |
| NON LOAD BEARING BUILDING ELEMENTS |  |
| EN 1364 -1 | Walls and external masonry |
| EN 1364 -2 | Ceilings |
| EN 1364 -3 | External curtain walls - Full configuration |
| EN 1364 - 4 | External curtain walls - Part configuration |
| LOAD BEARING BUILDING ELEMENTS |  |
| EN 1365 - 1 | Walls |
| EN 1365 - 2 | Floors and ceilings |
| EN 1365 - 3 | Beams |
| EN 1365 - 4 | Columns |
| EN 1365 - 5 | Balconies and walkways |
| EN 1365 - 6 | Stairways |
| NETWORKS |  |
| EN 1366 - 1 | Ventilation ducts |
| EN 1366 - 2 | Fire dampers |
| EN 1366 - 3 | Fire seals |
| EN 1366 - 4 | Linear joints fire seals |
| EN 1366 - 5 | Service ducts and shafts |
| EN 1366 - 6 | Raised floors |
| EN 1366 - 7 | Fire seal system for openings of transmission systems |
| EN 1366 - 8 | Smoke exhaust ducts |
| EN 1366 - 9 | Smoke exhaust ducts within a fire compartment |
| EN 1366 - 10 | Smoke control dampers |
| DOORS AND ROLLERS CONFORMATION |  |
| EN 1634 - 1 | Fire resistant doors and roller shutters |
| EN 1634 - 2 | Equipment for fire resistant doors |
| EN 1634 -3 | Smoke control doors |
| ROOFS IN EXTERNAL FIRE |  |
| ENV 1187 | Fire performance of roofs exposed to external fire |
| CONTRIBUTION TO THE FIRE RESISTANCE OF LOAD BEARING BUILDING ELEMENTS |  |
| ENV 13381 - 1 | Membrane protection - Horizontal |
| ENV 13381 - 2 | Membrane protection - Vertical |
| ENV 13381 - 3 | Concrete elements |
| ENV 13381 - 4 | Steel elements |
| ENV 13381 - 5 | Concrete/steel sheet composite elements |
| ENV 13381 - 6 | Concrete filled steel hollow columns |
| ENV 13381 -7 | Timber elements |

ANNEX D

## Reaction to fire - Euroclass system

Containing the fire within a building or within a fire compartment is sought by using low flammability materials. The determination of the predisposition of a construction product to contribute to the development and spread of fire is done through the system of the European classes (Euroclass), which allows the classification of construction products for ‘reaction to fire’ (reaction to fire) in accordance with Commission Delegated Regulation (EU) 2016/364 of 1 July 2015 ‘on the classification of construction products based on reaction-to-fire performance in accordance with Regulation (EU) No 305/2011 of the European Parliament and of the Council’.

Reaction to fire is an essential characteristic of construction products directly related to the second essential requirement for ‘fire safety’ construction works set out in Annex I to Regulation (EU) No 305/2011 and is provided for by the manufacturer as a class of performance (euroclasses) in the declaration of performance referred to in Article 6 of that Regulation.

In the classification system of construction products in relation to their reaction to fire a series of standard laboratory tests are used, which are defined in delegated regulation (EU) No 2016/364 and the ELOT EN 13501 standards, in their current version. The ELOT EN 13501 standard includes the categories and performance criteria as to the reaction to fire for construction products (ΕΝ 13501-1), floors (ΕΝ 13501-1), linear thermal insulation products for pipes (ΕΝ 13501-1), roofs (ΕΝ 13501-5) and electric cables (ΕΝ 13501-6).

A construction product's performance in relation to its reaction to fire within the Euroclass system is classified according to three criteria:

1. "Contribution to ignition and fire"

According to the Euroclass system, construction products are classified in seven main categories, according to how much they contribute to the ignition and spread of fire. These seven categories, in descending order, are as follows: A1, A2, B, C, D, E και F. The Α1 and Α2 classes include materials that have the least possible contribution to fire, i.e. virtually non-combustible materials, whereas class F includes those materials with the highest contribution to fire.

2. "Contribution to smoke production"

According to the Euroclass system, construction products are classified in three sub-categories, according to how much they contribute to smoke production:

s1: Zero or minimum smoke production

s2: Medium smoke production

s3: Considerable smoke production

3. "Contribution to the production of flaming particles or droplets"

The burning of some construction products, such as wood or thermoplastics, can create flaming particles or droplets which help spread the fire in areas far from where it originally started. According to the Euroclass system, construction products are classified in three sub-categories, according to how much they contribute to the production of flaming particles or droplets:

d0: No contribution to the production of flaming particles or droplets

d1: Small contribution to the production of flaming particles or droplets

d2: Considerable contribution to the production of flaming particles or droplets

Construction products within the European system are classified in relation to their reaction to fire by assigning a combination of symbols that provide information on the behaviour of the product in relation to the spreading of fire (Α1, Α2, Β, C, D, E, F), the production of toxic fumes (s1, s2, s3) and the production of flaming particles/droplets (d0, d1, d2). All possible combinations in the construction products classification system (excluding for floor coatings) in relation to their reaction to fire are shown in Table D.1. To classify a construction product in each category, the results of standard laboratory tests are taken into consideration, using proper criteria, as they are presented in the ELOT EN 13501 standard.

Table D.1: Possible combinations of the Euroclass system for the classification of construction products in relation to their reaction to fire.

| A1 |  |  |
| --- | --- | --- |
| A2 - s1, d0 A2 - s2, d0 A2 - s3, d0 | A2 - s1, d1 A2 - s2, d1 A2 - s3, d1 | A2 - s1, d2 A2 - s2, d2 A2 - s3, d2 |
| B - s1, d0 B- s2, d0 B - s3, d0 | B - s1, d1 B - s2, d1 B - s3, d1 | B - s1, d2 B - s2, d2 B - s3, d2 |
| C - s1, d0 C- s2, d0 C - s3, d0 | C - s1, d1 C - s2, d1 C - s3, d1 | C - s1, d2 C - s2, d2 C - s3, d2 |
| D - s1, d0 D- s2, d0 D - s3, d0 | D - s1, d1 D - s2, d1 D - s3, d1 | D - s1, d2 D - s2, d2 D - s3, d2 |
| E |  | E - d2 |
| F |  |  |
| Note: E category products are considered as smoke producing products and are not examined under the "s" criterion. |  |  |

For floor coatings, all possible combinations in the classification system in relation to their reaction to fire are shown in Table D.2.

Table D.2: Possible combinations of the Euroclass system for the classification of floor coatings in relation to their reaction to fire

| A1FL |  |
| --- | --- |
| A2FL- s1 | A2FL- s2 |
| BFL- s1 | BFL- s2 |
| CFL- s1 | CFL- s2 |
| DFL- s1 | DFL- s2 |
| EFL |  |
| FFL |  |

In accordance with the delegated regulation (EU) No. 2016/364 and the standard ELOT EN 13501-1, for the classification of construction products and floors in terms of fire response, according to the system of European classes (Euroclass), it is required to perform a series of standard laboratory tests, which are mentioned in Table D.3.

Table D.3 Standard reaction to fire tests for the classification of construction products in the Euroclass system.

| Standard | Test | Use for classification in the Euroclass system |  |
| --- | --- | --- | --- |
| ΕΝ ISO 1182 | Non combustibility test | A1, A2 | A1FL, A2FL |
| EN ISO 1716 | Determination of higher calorific potential | A1, A2, B | A2FL |
| EN 13823 | Single burning item test | Α2, B, C, D | - |
| EN ISO 11925-2 | Ignitability test | B, C, D, E, F | BFL, CFL, DFL, EFL, FFL |
| EN ISO 9239-1 | Heat radiation test on floorings | - | A2FL, BFL, CFL, DFL |

According to Commission Decision 96/603/EC of 4 October 1996 'establishing a list of products belonging to classes A 'No contribution to fire' provided for in Decision 94/611/EC implementing Article 20 of Council Directive 89/106/EEC on construction products (OJ L 267, 19.10.1996, p. 23 et seq.), there are materials which are classified directly in Classes A1 and A1FL as, due to a low degree of flammability, they are considered to have a ‘zero contribution to fire’. For all these materials, which are listed in the Table D.4, the relevant laboratory tests are not required for their classification in terms of fire reaction.

Table D.4: Non-combustible materials (Α1, Α1FL) for which no laboratory tests are required.

| - Expanded clay - Expanded perlite - Expanded (swollen) mica (vermiculite) - Rockwool - Foamed glass - Concrete - Concrete aggregates (mineral aggregates for heavy and light concrete excluding thermal insulation) - Concrete foam elements - Cement - Lime - Blast furnace slag/flying ash - Mineral aggregates - Iron, steel and stainless steel - Copper and copper alloys | - Zinc and zinc alloys - Aluminium and aluminium alloys - Lead - Gypsum and gypsum coatings - Mortars with inorganic binders - Elements of clay - Lime-lime elements - Natural rock and slate products - Building blocks of plaster - Mosaics - Glazing - Glass-ceramic products - Ceramic products |
| --- | --- |

Second Article

This Decree shall enter into force three (3) months after its publication in the Government Gazette.

The Minister for the Environment and Energy shall be responsible for publishing and implementing this Decree.

Athens, 10 May 2017

THE MINISTER

FOR THE ENVIRONMENT AND ENERGY

GEORGIOS STATHAKIS

THE DEPUTY MINISTERS

OF THE ECONOMY AND DEVELOPMENT 	OF THE INTERNAL AFFAIRS

ALEXANDROS CHARITSIS			 NIKOLAOS TOSKAS