TECHNICAL SPECIFICATIONS

OF THE DISTRIBUTION SYSTEM OPERATOR

VÝCHODOSLOVENSKÁ DISTRIBUČNÁ, A.S.

effective from 20 October 2022

The relevant provisions of Chapter 4.3 in Annex 3 The rules governing the connection of resources to the DS are defined in accordance with Decision No 0017/2018/E-EU of the Regulatory Office for Network Industries

Košice, 20 September 2022

Contents

1.	Initial provisions, basic definitions and abbreviations	3

1.1	Definitions	3

1.2	A list of abbreviations used in the document	4

2.	Technical specifications for access and connection to the distribution system	5

2.1	Method of connecting DS users for individual voltage levels	5

2.2	Voltage quality in the DS, user equipment requirements, and effect of the equipment on the DS	8

2.3	Technical specifications for connecting and operating generating equipment	9

2.4	Technical requirements for connecting local distribution systems	13

2.5	Connection point, measurement point, measurement method, and specified measuring instrument type	13

3.	Technical specifications for distribution system operation	14

3.1	Details on metering sets, measuring schemes, and specified measuring instruments	14

3.2	Instrumentation requirements	15

3.3	Assurance of supply quality parameters	15

3.4	Details on monitoring consumption point parameters	15

3.5	Exchange of operational information	15

3.6	Central control conditions for the operator of the transmission system and distribution systems	18

4.	Technical specifications for measurement in the distribution system	19

4.1	Control Centre metering	19

4.2	Conditions for installing commercial metering	20

5.	Technical specifications for the provision of universal service	20

6.	Technical specifications for interruption of electricity supply	20

6.1	Reasons for interruption or restriction of electricity supply from a technical perspective	20

6.2	Reasons for interruption or restriction of production of electricity sources from a technical point of view	20

6.3	Procedures for planned reconstruction and repair of distribution system installations	21

6.4	Planning and preparation for DS operation in a defined territory	22

6.5	Notification of power interruption or restriction	22

6.6	Procedure in the event of accidents and faults of DS facilities and the method of rectifying their consequences	22

7.	Technical specifications for disconnection from the distribution system	23

7.1	Reasons for disconnection from the System relating to technical factors	23

7.2	Procedure in the event of non-compliance with safety and operating regulations	23

7.3	Technical procedure for disconnection from the distribution system	23

8.	Technical specifications for distribution system control	23

8.1	Operational control of DS operation within a specified area	23

8.2	Regulation of voltage and reactive outputs in the ES SR and DS in a specified area	24

8.3	Operative changes to the electrification system connection schema	24

8.4	Steps for taking a DS user's equipment out of operation and placing this equipment back into operation	25

8.5	Work and records of work on a DS user’s electrical equipment	27

8.6	Responsibilities of shift personnel when on duty and during shift changes	27

8.7	Principles for keeping service records for a DS user's electrical equipment	27

8.8	Operating instructions, local operating regulations, and other binding documentation for central control	28

8.9	Principles of archiving central control documentation	28

9.	Technical specifications for SCADA, stipulation of requirements for the collection and delivery of information of central control of DS user equipment	29

9.1	Supervisory control and data acquisition for the ES (SCADA)	29

10.	Technical specifications for stipulating technical safety criteria for the DS	29

10.1	Safety when working on distribution system facilities	29

10.2	Safety in managing the distribution system	30

10.3	Construction safety	31

10.4	Preventive fault propagation plan and restoration plan after a system outage	31

10.5	Limiting consumption in emergency situations	31

10.6	Distribution system operating conditions in emergency situations	33

10.7	Distribution system tests	33

10.8	Development and renewal of the distribution system	34

ANNEX 1 The quality of electricity in the distribution system and its evaluation	37

ANNEX 2 Instrumentation requirements	40

ANNEX 3 Rules for connection of sources and electricity storage facilities to the DS	42

ANNEX 4 Specifications for measuring electricity	87

# Initial provisions, basic definitions and abbreviations

These Distribution System Operator Technical Specifications (hereinafter 'DSO TS') for Východoslovenská distribučná, a.s., are a document produced by this entity pursuant to Act No 251/2012, on energy and on changes to some acts, and pursuant to Act No 250/2012, on regulation in network industries, as amended, focuses on addressing selected distribution system (hereinafter 'DS') management, operation, and development problems.

Decree No 271/2012 of the Ministry of Economy of the Slovak Republic lays down the details of the scope of the Technical conditions for access, connection to the system and the rules on system operation. The DSO TS is a binding document for all distribution system users, and pursuant to § 2(1) of Decree 271/2012 specifies minimum technical design and operating requirements for connection of electrical power equipment to the DS. If the DSO TS refer to fixed (numerical) values, technical properties, or specific technical standards related to electromagnetic compatibility, individual references have an indicative or informative nature that is based on recommended best practices. The requirements of these DSO TS, cited Slovak technical standards (STN) and European standards (EN) are indicative and are also considered to have been met if conditions of equivalent technical standards issued or recognised by authorities of the Member States of the European Union, the European Economic Area or Turkey have been met.

Terms that are defined for the electricity sector in Act No 251/2012, on energy and on amendments to certain laws, as amended (hereinafter the ‘Energy Act’); in Act No 309/2009, on the promotion of renewable energy sources and highly efficient combined production and on amendments to certain laws, as amended (hereinafter ‘Act No 309/2009’); and in Decree No 24/2003, laying down the rules for the functioning of the internal market in electricity and the rules for the functioning of the internal gas market, as amended (hereinafter the ‘Market Rules’), have the same meaning in these DSO TS.

Definitions

Electricity facilities of the applicant or a user - for the purposes of these DSO TS, is the common name for electrical consumption equipment of the applicant, or user of the DS, and facilities for electricity production or storage (accumulation).

DS operator central control (DSO CC) — a centralised workplace that manages DS operations.

DS operation management — is carried out by means of protective, control, measuring, information and telecommunications equipment. DS operation management uses intelligent system elements (automated or remotely controlled switching, metering, monitoring elements), with optical fibres as a priority communication layer, or taking into account the efficiency of renewal, development and operation of DS as well as GSM technologies.

An alternate source of electricity (hereinafter ‘ASE’) is a device for the production of electricity that is connected to the user’s electrical consumption equipment, where this device must not be operated in parallel with the distribution system. ASE is intended exclusively for powering electrical equipment during an outage in the distribution system.

A facility for the storage (accumulation) of electricity, for purposes of these DSO TS, is considered to be the following:

- a user's electrical consumption facility - being supplied with electricity from the DS (charging mode);

- electricity generation equipment – supplying electricity to the DS or to an electrical facility belonging to a DS user.

Distribution system operating regulations contain various operating data that can affect the user and require his cooperation. For example provisions on estimates of expected consumption, source outage planning, reporting of operating changes and events, ensuring occupational safety, operating safety, and emergency procedures.

Technical specifications for DS access and connection define the technical aspects of operating relationships between the DSO and all users connected to the DS in order to ensure non-discriminatory, transparent, and safe system access, connection, and operation.

A list of abbreviations used in the document

SCADA	Supervisory control and data acquisition

CC	Central control

CBC	Central backup control

MP	Management plan

DSO CC	DS operator's control centre

TSO CC	TS operator's control centre

DS	Distribution system

DTS 	Distribution Transformer Substation

EN 	European standard

ES	Electrical system

EE	Electrical equipment

FT 	Functional tests

PVPS	Photovoltaic power station (a facility for producing electricity using solar energy)

MIP	Main isolation point

LOR	Local operating regulations

MRC	Maximum reserved capacity

IVT	Instrument voltage transformer

ICT	Instrument current transformer

LV	Low voltage

ASE	Alternate source of electricity

ECF	Electrical consumption facility

DSO 	Distribution system operator

OI	Operating instructions

PN	Total installed output of the electricity production equipment

DSO OR	DSO operating regulations

TSO	Transmission system operator

TS	Transmission system

MS	Meter switchboard

DP	Disconnect point

STN 	Slovak technical standard

TI	Technical inspection

TSC	Technical specifications for connection

DSO TS	DS operator’s technical specifications

RONI	Regulatory Office for Network Industries

SPS	Substantive plan and schedule

HV	High voltage

VHV	Very high voltage

BD	Binding documentation

EHV 	Extra-High Voltage

RfC	Request for Connection of electrical power equipment

# Technical specifications for access and connection to the distribution system

Connection, access, and use of devices and their components by DS system users, operators of electricity installations, or third parties is subject to the written consent of the DSO and the consequent fulfilment of all technical and commercial conditions of the DSO.

  - Method of connecting DS users for individual voltage levels

An applicant for connection of electrical equipment must request the DSO to stipulate technical specifications for connection (TSC) on the prescribed form. The DS operator defines the draft TSC, which is part of the contract for connection of the applicant’s electrical power equipment. The draft TSC for electrical equipment that will either consume or generate electrical power (hereinafter jointly designated as the applicant’s or user’s ‘electrical power equipment’) to be connected to the DS must comply with, among other things, the DSO’s technical specifications and the DSO’s operating regulations.

Only electrical power equipment that has a valid Connection Contract can be connected to the DS.

An electrical connection is a branch-off from the DS to the first breaker element (LV) or switching element (VHV, HV) that is part of the DS. The electrical connection shall be established by the DSO and shall be owned by the DSO. The type of standard connection at a supply point depends on the nominal voltage of that part of the DS to which the supply point is connected.

Electrical power equipment located past the breaker/switching element is a supply line and must be connected and operated in accordance with the DSO's technical specifications and commercial terms and conditions. The costs of the supply line are always borne by the applicant and the supply line is their property.

This chapter describes the standard ways of establishing/modifying an electrical connection, and modifications in the DS due to the requirements for a new supply point or an increase in MRC. The applicant participates in these modifications through a connection fee stipulated by applicable legislation.

The owner of the supply line must ensure its operation, maintenance, and repair in such a manner that the supply line does not present a risk to human life, health, and property and does not cause malfunctions in the DS.

In principle, the applicant is assigned one connection point to the distribution system. The DSO decides the applicant’s connection location and method.

- Connection to the LV grid

In the case of outdoor power lines, the connection is made by branching off from the outdoor power line or from a breaker cabinet. The connection ends at the breaker element that is part of the DS.

In the case of cables, the connection is made by branching off from the cable or from a breaker cabinet. The connection ends at the breaker element that is part of the DS.

The electrical connection is either a standard suspension cable or an insulated conductor. The minimum mathematical cross-section of an LV electrical connection is 16 mm2.

The DSO stipulates the connection method based on technical conditions at the connection point (the number of new connections, the need for disconnecting locations, the method of operation, the prospect of connecting other new subscribers, etc.).

- Connection to the HV grid

Connection to the HV grid is only possible if there is insufficient LV capacity in the given area and it cannot be provided through modifications to the DS, or such modifications are not more cost-effective or technically more efficient connection to the LV grid. Connection to the HV grid is also possible if the nature of the effects of the applicant’s electrical power equipment on the grid requires such a connection.

In the case of outdoor HV power lines, the connection is made by branching off from the distribution line, and in this case the electrical connection ends with an HV switching element that is owned by the DSO. The implementation method is governed by a separate contract between the DSO and the DS user.

In the case of cables, the connection is made by branching off from the distribution line or branching off from the distribution switchboard array, which in this case provides the electrical connection, or by branching off from the distribution line (looping). Operation of user equipment connected by looping is ensured by a responsible individual with the necessary qualifications, and is regulated in the LOR.

The electrical connection is normally made with an AL/ST (AlFe) conductor, a cable, or an insulated conductor. The minimum mathematical cross-section of an HV electrical connection (pertaining to the Al content) is 40 mm2.

- Connection to the VHV grid

Connection to the VHV grid is only possible if there is insufficient HV capacity in the given area and it cannot be provided through modifications to the DS, or such modifications are not more cost-effective or technically more efficient connection to the VHV grid. Connection to the VHV grid is also possible if the nature of the effects of the applicant’s electrical power equipment on the grid requires such a connection.

In the case of cables and outdoor power lines, the supply point connection is made by connecting to a substation or by looping distribution lines.

The process of selecting the method for connecting the electricity consumer’s consumption equipment at the VHV voltage level is based on the magnitude of connected power, the network configuration at the anticipated connection location, and the customer’s requirements for the degree to which the power supply is guaranteed. Outdoor lines are the standard method used for VHV connections.

Connection of a customer at the VHV level is usually addressed as follows:

- by creating a single connection to an existing VHV substation belonging to the DSO; the connection begins by branching from 110 kV busbars and includes a feeder bay including associated equipment. The end of the electrical connection consists of attachment points for the applicant's supply conductors (phase conductors and ground cables) at the substation portal, as well as points at which the substation’s current circuits are connected to the applicant’s VHV supply conductors;

- by looping VHV lines to the user’s VHV/HV substation, there is no separate electrical equipment physically representing the electrical connection, and involves a direct connection from the DS. In this case, the boundary between the user’s equipment and the VHV lines owned by the DSO consists of phase conductor attachment points and ground cables at the substation portal, as well as points at which the current circuits of the user’s substation are connected to the DSO’s VHV power lines.

- Special connection

Special connection of grid users with special electrical distribution requirements can be established if the DS user has a need for backup power. If an applicant for connection of electrical power equipment requests a connection to more than one point in the distribution system, for example, through another distribution or supply line; or if the applicant’s electrical power equipment is already connected and the applicant is receiving the desired amount of electricity, but is requesting connection to a different voltage level or to a different point at the same voltage level, and this requirement is not due to changes to technical specifications of the connection, this is a special connection. Connection of a grid user to the VHV and HV grid through looping, if in the given case such a connection method is defined by the DSO, is not considered a special power connection.

A special connection to the distribution system is contingent on signature or amendment of a connection contract. Any automatic back-up power supply (i.e. automatic change of the connection point when over-connected) of a DS user shall be approved by the DSO prior to connection.

- Electrical protection

To ensure reliable and safe operation of the distribution system and of system users' equipment, it is necessary to install electrical protection elements on the VHV switchboard bays at the supply point, the configuration of which is specified by VSD, a.s. If protection is engaged following a short-circuit, the switch in the relevant bay in the VHV switchboard must trip automatically. Switches in VHV conductor bays are normally 3-actuator and include automatic reconnection; their configuration is specified by VSD, a.s. In justified cases VSD, a.s. can approve the use of single-actuator switches. Short VHV conductors must be protected using reliable protection, for example using differential protection. In other cases distance protection will suffice, with transmission equipment to ensure protection trip logic.

- Normative framework

Electrical connections, their design capacity and protection must correspond to the relevant regulations, especially:

STN 33 2000: Electrical engineering regulations,

STN 33 3320: Electrical connections

STN 33 3051: 1992 Protection of electrical equipment and distribution facilities.

- Local operating regulations (LOR)

The applicant for connection, user, or operator:

- of VHV and HV electrically powered equipment; and

- equipment for the generation or storage of VHV, HV, and LV electricity with installed output greater than 11 kW;

- other equipment located at the DS facilities or part thereof (communication and optical networks, public lighting, intercom, transmitters, monitoring systems, etc.)

at least 30 days prior to a planned technical inspection of equipment, must submit local operating regulations for electrical power equipment to the DSO for approval in electronic form to the email address defined in the statement from the DSO. The company’s contact departments for sending LOR by the applicant or user of the grid are as follows:

- VHV electrical equipment: 			Technical development

- HV and LV electrical equipment: 			Management of Investments

- third-party equipment that is implemented 
as part of the DS:				The operator of the relevant part of the DS

The DSO shall ensure the LOR are commented on within 15 days, and shall send the comments to the equipment connection applicant. The DSO shall ensure each additional assessment of changes to LOR takes place within 15 days from receipt of the modified version of the LOR.

If the DSO approves the LOR for electrical equipment belonging to the connection applicant, they can then ask the DSO to schedule it at least 5 workdays prior to the planned technical inspection of the equipment.

LOR for electrical equipment take effect only after they have been approved by all stakeholders, where the applicant for connection of electrical equipment shall deliver these LOR in printed from, approved and signed by all affected parties (the author of the LOR, the equipment operator, and DSO personnel) no later than during the technical inspection of the equipment.

Without approved LOR, equipment belonging to a connection applicant, user, or operator cannot be commissioned and brought under DS control within the scope of management of the DSO.

- Verification of compliance with technical specifications for connecting users to the DS.

The DSO reserves the right to check compliance with technical specifications stipulated for the DS user's electrical equipment, and for this reason reserves the right to perform a technical inspection and functional test of the user's equipment.

Supplementary requirements for power generation facilities are governed by Annex 3 to this DSO TS.

Voltage quality in the DS, user equipment requirements, and effect of the equipment on the DS

Due to the fact that in a distribution system power grid all elements and equipment are galvanically interconnected, in order for them to function correctly they must be mutually electromagnetically compatible pursuant to Directive of the European Parliament and of the Council 2014/53/EC, and Slovak government decree No 127/2016 on electromagnetic compatibility. The equipment or device may not generate electromagnetic interference which would prevent the conventional use of other equipment and must also be sufficiently resistant to interference which can be anticipated in the DS. DS users may only put facilities into operation whose mains pollution does not have a negative effect on voltage quality in the DS and on its users. If the DSO detects that the permissible levels of mains pollution have been exceeded, the user shall take the necessary corrective measures. Otherwise, the DSO may limit or interrupt electricity distribution to such a user.

The highest levels of effects on the DS caused by a user of the grid are generally defined as follows:

A relative change in the effective voltage value:

Δumax ≤ 2 % Un for VHV and HV voltage levels

Δumax ≤ 3 % Un for the LV voltage level

Degree of flicker perception - user contribution

Long-term flicker perception Plt ≤ 0.5 for HV and LV

Short-term flicker perception Pst ≤ 0.8 for HV and LV

For VHV, the degree of back effects is specified according to the nature of the grid at the connection and user equipment location, with the greatest permissible user-contributed value being Plt ≤ 0.6.

Degree of voltage asymmetry - user contribution

The greatest degree of user contribution is 0.7 % ( = the greatest degree of mean ten-minute effective values of the back component compared to the positive voltage component) for HV and LV. The degree of voltage asymmetry at the VHV level is chosen with respect to the nature of the grid and the user’s equipment at the given location, but it must not exceed 1.5 %.

Degree of voltage and current harmonics

The contribution of the grid user’s equipment to the total harmonic voltage distortion factor may be at most 2.5 %.

Higher-order harmonic currents emitted by the grid user’s equipment may achieve maximum values in the grid given by the following relationship:

Iharm ≤ IZ*kharm*√(Sk3“/SZ),

where Iharm is the relevant harmonic current, Lz is the total equipment current, ‘Sk3’ is the three-phase short-circuit power at the point the equipment is connected to the DS, and Sz is the total power output of the equipment. Maximum contribution values from the grid user to individual voltage harmonic components and the parameter kharm are given in the following table:

| Order | 3 | 5 | 7 | 11 | 13 | 17 | 19 |  | Total |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Uharm. /%/ | 1.25 | 1.5 | 1.25 | 0.9 | 0.75 | 0.5 | 0.45 |  | 2.5 |
| Kharm (-) | 0.006 | 0.015 | 0.010 | 0.005 | 0.004 | 0.002 | 0.0015 |  | - |

In the case of specific types of rectifiers, inverters, etc. with assumed higher back effects, or an already recorded higher degree of effects, the DSO has the right to define a broader range of parameters or stricter limits for harmonics.

Equipment connected to an HV or LV grid must have immunity to supply voltage dips and interruptions defined in STN EN 50160 so that this equipment does not experience functional failure or cause other subsequent damage during the expected frequency of dips and interruptions specified in STN EN 50160. Automated switching practices in the DS in connection with transient faults and prevention of serious failures in the DS may cause declines down to 40 % of the nominal supply voltage and supply voltage interruptions of up to 1 s. The DSO shall not be liable for any damage arising from supply voltage dips and interruptions subject to the provisions of STN EN 50160. At the same time, relevant equipment belonging to grid users should have resistance to voltage dips that complies with the provisions of IEC 61000-4-34.

A DS user must operate technology and other equipment consuming electricity in a manner that prevents this equipment from having negative effects on the DS under existing minimum technical and operating grid parameters at the user/DSO interface that would exceed the limits specified in Annexes 1 (equipment consuming electricity) and 3 (equipment generating electricity) of this TS. If these limits are exceeded, the DS user must implement additional measures in the area of eliminating negative effects in order to eliminate their negative effect on the DS and other DS users. The DS and users’ electrical equipment must be designed so that all required qualitative voltage characteristics at common connecting points of subscribers at all voltage levels comply with the requirements specified in Annex 1 to these TS.

During fault states, a temporary change in power supply, and activities in the TS, DS, and connected facilities due to emergencies in relevant systems, transient deviations of qualitative voltage parameters from values defined in this regulation may occur. The values specified in the DSO TS do not apply to these fault states.

If a DS user installs and uses devices for transmitting signals superposed on the electrical network, these devices must meet STN EN 50065 including its addenda. If the user proposes to use said equipment for superposed signals in the framework of the DS, prior consent of the DSO is required. The use of said equipment for transmitting information throughout the DS must not affect power quality in the DS. The relevant equipment may only be operated with the DSO’s consent.

A user whose equipment has been proven to have a negative effect on voltage quality in the DS to the extent that limits stipulated in this chapter are exceeded must correct the situation or disconnect equipment causing these effects from the DS, either immediately or by a deadline agreed upon with the DSO. If the situation is not corrected within the agreed-upon period and the negative situation still exists, such a user will be disconnected, or will have his distribution of electricity from the DS interrupted in accordance with the Connection Contract.

Technical specifications for connecting and operating generating equipment

Power generation equipment (hereinafter a 'source') is classified into two basic groups based on its operation with the DS:

- with parallel operation with DS — this includes a so-called hybrid system (Annex 3), a small source of electricity and a local source as defined in the relevant legislation. This category also includes electrical accumulation equipment operating in power supply mode.

- not in parallel with the DS (island operation outside the DS) – these, for example, include alternate sources of electricity or island systems.

Generating equipment working in parallel with the DS – its connection is contingent on compliance with the DSO’s technical specifications and commercial terms and conditions of the DSO. One of the basic technical specifications for assessing the ability to connect a source to the DS is the degree of its back effects on the grid from the perspective of relative voltage changes. The highest permissible values of relative voltage change Δu, caused by the connection of the source, are set for each voltage level in Chapter 2.2.

During fault conditions, temporary supply changes, and work being done on the TS, the DS, equipment connected to them due to emergencies in relevant systems, transient deviations from the above values of Δu at the source connection point, where Δu may reach a maximum of 5 %.

Categorisation of sources from the perspective of their overall active installed PN output and voltage level at which they are connected to the DS:

| Category (Type) pursuant to Commission Regulation 2016/631 | Maximum capacity threshold | Voltage level of the DS connection point |
| --- | --- | --- |
| A | 0.8 kW ≤ PN < 100 kW | < 110 kV |
| B | 100 kW ≤ PN < 5 MW | < 110 kV |
| C | 5 MW ≤ PN < 20 MW | < 110 kV |
| D | PN ≥ 20 MW | < 110 kV |
|  | Irrelevant | ≥ 110 kV |

Table 1 Categorisation of sources from the perspective of their installed output and voltage level at which they are connected to the DS

PN is the total installed output of the power generation equipment specified in the Contract for connection of power generation equipment to the distribution system.

Example: If power generation equipment connected to the DS (<110 kV) has a total installed output of PN=10 MW and comprises ten 1 MW generation units (alternators, inverters), each power generation unit must comply with the parameters for Type C pursuant to stipulated power levels.

Further technical specifications for connecting and operating generating equipment are also specified in Annex 3 to these DSO TS.

Before putting a source into operation, the operator must also draw up LOR, which among other things will define the obligations and procedures of the source operator and the DSO during the operation of power equipment and emergency operating conditions. The equipment operator must submit the local operating regulations for approval to the DSO pursuant to the conditions specified in Chapter 2.1. When drawing up local operating regulations for a source, the following is taken into account:

- the source type and its operating options;

- DS operating requirements;

- legitimate interests of the source operator;

- compliance of source operation with Slovak energy policy.

Alternate sources of electricity – the operator of an ASE must provide reliable technical and electrical separation of the electrical consumption equipment (the backed-up part of the installation) from the DS during its voltage-free state when such a source is in operation. During its operation the ASE must not transfer any voltage to the DS. Parallel operation of ASE with the DS is forbidden, including during its connection/disconnection to/from the ASE operator's utilising equipment.

The DSO defines specifications for ASE connection. The ASE operator must perform a functional test of such a source with the participation of DSO representatives. The purpose of the ASE test is to check that technical specifications for ASE connection to the consumption equipment have been complied with, especially a check of whether blockage of parallel ASE/DS operation is functional. The result of the functional test is recorded in a specified record that the DSO publishes on its website.

ASE operation is governed by the LOR for the relevant consumption equipment. Any change to the technical parameters of the ASE, a change in the way it operates, termination of operation, and change to the blocking of parallel operation with the DS must be approved by the DSO. A necessary prerequisite is also subsequent approval of relevant consumption equipment technical documentation, or of the ASE and updated LOR by the DSO. The DSO performs a new functional test when ASE parameters change.

The ASE operator is responsible for the quality of voltage in consumption equipment during its operation and damage to the consumption equipment or to the DS due to ASE operation.

Island systems must not operate in parallel with the DS and the relevant installation, including electrical consumption equipment, or the relevant installation for the system’s own consumption must be permanently mechanically and electrically separated from the DS (no conductive or magnetic connection to the DS) not only from the point of view of the phase conductors, but also from the point of view of neutral, protective conductors and auxiliary circuits. Mere galvanic isolation of such systems from the DS is not sufficient. For such systems, the DSO does not define connection conditions, does not perform technical inspections or functional tests, and does not require notification of their connection or commissioning.

- Requirements for source operating parameters

The requirements for electrical parameters specified in the Technical Specifications of the Transmission System Operator apply to sources controlled by the TSO CC. For other producers outside the DS, the requirements for electrical parameters measured at the generator unit terminals are defined according to connection method and are specified by the DSO during negotiations regarding connection. Basically, the source being connected must, like all other equipment, comply with requirements stipulated by Order of the Government of the Slovak Republic No 194/2005 and No 318/2007.

During planned renovations, repairs, maintenance, and inspection of the relevant part of the DS, at the request of the DSO, the source operator shall, if the circumstances so require, disconnect the source from the distribution system. The DSO must notify the source operator in accordance with the relevant provisions of the Energy Act.

The DSO shall specify in writing whether for controlling source voltage, a continuously operating rapid-response instability-free excitation system is required over the entire operating range of the source. This depends on the size and type of the source and the adjacent parts of the DS to which it is connected. The DSO shall specify in writing any requirements for voltage control coordination at the DS node.

- Coordination with existing protective devices

If there are protective devices for the source, it will be necessary to coordinate them with the protective devices of the DS as follows:

- in case of sources connected to the DS, the electrical energy producer must adhere to cut-off times of the fault current running to the DS so as to minimise the impact of outages in the producer's equipment on the DS. The DSO shall ensure that the generation protection settings meet the DSO's own cut-off times. The required cut-off times of outages are measured from the time the fault current until it is permanently interrupted (arc extinction), and are specified by the DSO in such a manner that they will meet the requirements for the applicable part of the DS;

- prior to connection, the DSO and the user shall reach a written agreement during consultations on the settings of the protective devices controlling the cut-off switch or on the settings for the switching device (for purposes of backup power) at any point of connection to the DS system. These values cannot be changed without the prior consent of the DSO;

- if there are protective devices for the source, it is necessary to coordinate them with any automated reclosing specified by the DSO;

- protective devices for sources must not engage in the event of short-term asymmetry caused by elimination of a fault by backup protection;

- the DSO shall notify a future electrical energy producer of the magnitude of potential voltage asymmetry in the network when defining connection specifications.

- Requirements for cooperation with control and information systems

Sources with a total installed output of 100 kW and higher (source types B, C and D) connected in parallel to the DS must comply with the requirements of standardisation of control and information systems of control rooms and operator power facilities:

- all switching elements on the VHV and HV route and as well as LV lines on the route from the DS to individual generators must use two-bit signalling (INTERMEDIATE POSITION-OFF-ON-FAULT). Grounding switches in substations must be equipped with signalling; manual control is sufficient, with safeguards against erroneous use. The state of all breakers along this route must be indicated remotely using one-bit signalling (ON-OFF);

- if automatic backup equipment is installed, remote signalling is provided indicating its state (on/off), that automatic backup power is engaged, and its remote control is provided (Switch on/Switch off);

- if overcurrent protection is installed, the presence of short-circuit current and of a ground fault are signalled. Threshold current values for fault assessment must be configurable;

- all remote control and transmission equipment must have backup power (backup duration of at least 10 hours and the ability to handle at least 10 OFF/ON switching cycles for all remotely controlled elements);

- all remotely controlled equipment must have a local control option in case of a communication fault:

- power facilities must have blocking conditions in place for the control of individual elements taking into account technical requirements and operating modes. These blocks mainly include blocking of remote control during local mode and vice versa, blocking grounded terminal activation, blocking automatic backup power if a fault is detected on the backup power terminals or if they are grounded, and blocking of remote control and control system control during manual operation of a switching element;

- the facility must have a main isolation point (MIP) that disconnects the production portion of the source in such a manner that power required to start up the generators remains available (if possible). the MIP must be designed for the nominal switched power value. The MIP must be remotely controlled by a ‘switch off and block’ command, and after being switched off (by command, protection, etc.) it must be blocked from being switched back on. The dispatcher uses the ‘unblock’ command to unblock and permit switching on. Until this command is issued, the MIP cannot be switched on; more precisely, generators cannot be connected in any manner. Blockage of an MIP caused by network protection ends automatically after a certain fault-free amount of time has passed;

- where more than one MIP is used after metering equipment on the source installation (e.g. in the case of wind farms, local distribution systems, etc., where generators are deployed within a large area and where technical or spatial constraints prevent the use of one common MIP), it is necessary to ensure, in agreement with the DSO, that the parameters of all generators with a total PN greater than or equal to 100 kW (i.e. type B, C, D) are transferred to a single collection point with a range defined by VSD. The use of more than one MIP must be approved by the DSO, which assesses the difficulty of implementing a single MIP from the point of view of the output of a power source with multiple generators to the DS or data transfer to the DSO CC. One network protection may be installed to monitor system parameters and send a distributed shutdown command to individual MIPs, or each source will have individual network protection and MIP for all generators;

- it is signalled remotely using summary reports for MIP protection activation, and separately for individual generators;

- the connection of individual generators is signalled remotely (summary reporting of a chain of switching elements between the generator and the MIP). The schema will include generators along with block transformers;

- remote on-line measurement of the following quantities at the DS supply point is required from each production facility: ±P, ±Q, 3xUphase, 3xUcombined, 3xIphase, frequency, cos φ. If there are multiple possible power supply routes, this measurement must take place on each such connection to the DS;

- at the same time, remote on-line measurement of the terminal values of the generator itself is required to the extent of ±P, ±Q, 3xUphase, 3xUcombined, 3xIphase, frequency, cos φ;

- in the case of rotary generators, the measurements specified in the previous point must be performed separately on the terminals of each generator;

- wind farms will have signalling, measurement, and control in part of the system as in the substation;

- control system equipment in these facilities must have time synchronisation, and must at least be synchronised with an communication telegram from a higher-order control room;

- work for purposes of control will be measured by calculating the integral of work from effective values of P.

For sources with total installed output up to 100 kW (Type A sources) and for power consumption equipment, the DSO will perform an individual assessment of the need to connect the source to the DSO’s control system.

Technical requirements for connecting local distribution systems

When connecting local DS to regional DS, the rules for connecting electricity consumption equipment, sources and storage (accumulation) of electricity shall apply to the corresponding range according to the specification of the connected DS.

An applicant for connection of a local DS can connect this DS only if it meets the DSO’s technical specifications and commercial terms and conditions (DSO OR, DSO TS, and others), and in doing so must:

- apply for connection of consumption equipment, electricity storage equipment and sources using the prescribed forms;

- submit all relevant levels of design documentation of the given electrical equipment to the DSO for approval;

- submit the LOR of the local DS to the DSO for approval.

The DSO reserves the right to verify compliance with technical specifications for connection stipulated for the local DS, and for this reason reserves the right to arrange a technical inspection of the consumption equipment or to arrange a technical inspection and functional test for sources with installed output greater than 11 kW.

Connection point, measurement point, measurement method, and specified measuring instrument type

A detailed description of electricity measurement requirements is provided in 'Podmienky merania elektriny' [Electricity Measurement Specifications] on the DSO's website https://www.vsds.sk/edso/domov/technicke-info/meranie-distribucie/suvisiace-dokumenty.

Before connecting to the DS, the subscriber must establish a measuring point at their own expense that encompasses all circuits and design components of the metering system other than the electricity meter and communications equipment, which are supplied by the DSO. The measuring point is usually established at the ownership boundary between the subscriber and the DS for purposes of measuring the flow of electrical energy (in either direction). An electricity meter that serves as a specified measuring device for billing remains the property of the DSO. Other metering point equipment, including measuring transformers, shall be the property of the customer, unless agreed upon otherwise.

When establishing measurement, the subject follows the instructions of the operator of the system to which they will be connected and the instructions of the commercial measurement operator.

Commercial measurement and support is provided by the DSO, who must ensure aspects of measurement specified by applicable legislation are performed. For measurement purposes, a suite of equipment operated by trained personnel is used; this is termed a commercial measurement system.

Commercial measurement must be established in accordance with the DSO's applicable 'Electricity Measurement Specifications' located on the DSO's website. The measurement type and method is primarily determined by the voltage level at the measuring point and the value of the contractually agreed-upon maximum reserved capacity (MRC).

The technical implementation of metering, collection, transmission and recording of data shall be decided by the DSO. The DSO is responsible for making the commercial measurements.

Pursuant to applicable legislation, commercial measurement is performed only by specified measuring instruments, which must be operated pursuant to the Metrology Act, relevant decrees, and applicable STN. Depending on the measurement type and method, commercial measurement may be implemented using a suitable combination of specified measuring instruments: an electricity meter, and measurement and current transformers

# Technical specifications for distribution system operation

The operator of electrical equipment connected to the DS must upon the DSO's request provide proof that this equipment is technically sound and reports regarding technical inspections and tests of this equipment or parts thereof.

  - Details on metering sets, measuring schemes, and specified measuring instruments

A consumption point is considered to be electrical equipment that makes up a spatially or territorially enclosed and permanently electrically connected unit in which the flow of electrical energy is measured with one or more specified measuring instruments. If a permanently electrically connected unit is interrupted, it will also have to meet the condition of direct technological continuity.

The entity shall ensure adequately dimensioned access routes to the metering set on its premises for all involved parties.

Measurement must be transparent; all of the stakeholders have access to the measured values. The specific access solution must be agreed upon with the DSO.

Further details (accuracy of meter sets, etc.) are provided in the document ‘Electricity Measurement Specifications’ published on the DSO’s website.

In order to guarantee prompt installation of the measuring equipment, the subject shall arrange the positioning and type of measuring devices and instrument transformers with the DSO during the design process at the latest.

The entity shall provide the DSO with unobstructed access to the metering installation and related equipment.
The DSO is entitled to inspect the subject’s equipment up to the measuring equipment.

Based on a written request and under pre-agreed conditions, the DSO will allow an authorised subject to monitor data from the measuring equipment.

Instrumentation requirements

Details of instrumentation requirements are specified in Annex 2 to the DSO TS and in the document ‘Electricity Measurement Specifications’ published on the DSO’s website.

Assurance of supply quality parameters

Electrical power quality is defined as a set of selected voltage characteristics at a given point in the DS under normal operating conditions, compared with limit or with informative reference technical parameter values. These characteristics do not apply to abnormal operating conditions, including:

- temporary power arrangements to ensure the continuity of electricity supply to grid users under conditions that occur due to a fault, maintenance and construction work, or to minimise the extent and duration of power outages;

- cases when a system user's installation or equipment fails to meet relevant standards or technical specifications for connection stipulated by the system operator, including limit values of conducted interference;

- abnormal situations (extreme weather conditions, natural disasters, acts of third parties, orders from state administration authorities, force majeure, and during insufficient power due to external circumstances).

The required voltage characteristics of the electricity supplied for individual voltage levels are specified in Annex 1.

Details on monitoring consumption point parameters

The DSO is authorised to monitor the user’s effect on the DS. This monitoring generally concerns the magnitude and course of active and reactive power transmitted to the consumption point and for determining the level of back effects of the DS user’s equipment on the quality of electricity in the DS.

If the user supplies or uses active or reactive power to/from the DS that exceeds agreed-upon values for the consumption point, or through the operation of power equipment significantly worsens voltage quality parameters at the connection point, the DSO shall inform the user of this fact and shall also supply the results of the monitoring.

The user may request technical information on the monitoring method used. In cases where the user exceeds agreed-upon values, they must immediately restrict the consumption or supply (transmission) of real and reactive power to agreed-upon values and take corrective measures in order to reduce the negative effect of his equipment on DS voltage quality.

Even in cases where the user requests an increase to active and reactive power that does not exceed the technical capabilities of the consumption point, he must adhere to the maximum reserved capacity (requested power supply) pursuant to the current contract if he has not asked the DSO to change this contract and this change has not been technically implemented.

Exchange of operational information

Exchange of operating information must be arranged so that the consequences of activities or events can be recorded, and so that possible operating risks can be taken into account and assessed in order to ensure proper operation of the DS and the user’s system.

This part of the DSO TS applies to the DSO and DS users, who include:

- all other DSOs connected to this DS;

- subscribers connected at VHV or HV levels;

- electrical energy producers connected to the DS at VHV or HV levels.

- Communication

The DSO and the DS users agree on communication channels in order to ensure effective exchange of information.

Communication should be, if possible, directly between the user and the operator of the grid to which the user is connected.

- Requirement for information on activities

In accordance with the DSO's operating specifications, user connected to the DS must inform the DSO of any activity that could affect DS operation.

The DSO shall inform the user of any activity in the DS and/or the TS that could affect the operation of the user’s system connected to the DS.

Certain activity can be elicited by other activity or events in someone else’s system. In such a case, the information provided shall differ from information on an action taken independently.

Without prejudice to the general requirement of prior notice, the following examples are situations that have or could have an effect on actions in the DS or another system.

Therefore, the following information must be given:

- implementation of planned outages of equipment or instruments;

- breaker or cut-off switch functions or possible sequences or combinations thereof, temporary overloading, connection of systems or connection of a source;

- voltage control.

- Information format

Information about the actions shall describe them in sufficient detail and, even though the reason does not need to be specified, it must enable the recipient to assess and evaluate the impacts and risks arising from the action. The notification shall contain the name of the employee providing this information. The recipient may raise questions relating to clarification of the content of the notification.

Information that the DSO provides on activity in the DS that is initiated by another activity (the initial activity) or an event in the DS user’s system shall describe the activity and contain information that the DSO has received from the DS user in relation to the initial activity or event in his system.

Such information shall be sufficiently detailed as to enable the recipient to reasonably consider and assess the impacts and risks to the DS caused by the activity. It shall also contain the name of the DSO employee providing the information on the action.

The recipient may raise questions relating to clarification of the content of the notification.

If the user submits a message on an activity or event in his system caused by a random, proposed, or planned action in another subject’s system, his notification intended for the DSO shall contain the information that the DS user has received on the activity. This information may be passed on by the DSO.

Information that the DSO provides on an activity that is initiated by an activity or an event in the DS shall describe the activity and contain information that the DSO has received from the TSO in relation to the initial activity or event in the DS. Such information shall be sufficiently detailed as to enable the recipient to reasonably consider and assess the consequences and risks caused by the activity in the DS and must also contain the name of the DSO employee providing the information. The recipient may raise questions relating to clarification of the content of the notification.

The user may pass information contained in the notification from the DSO on to the electrical energy producer with a source connected to his system or to another DSO to which he is connected in the event that this is required by contractual connection conditions.

Other than in the aforementioned cases, the DS user may not transfer information contained in the DSO’s notification or in the notification of another DS user who obtained it from the DSO to anyone connected to his system. He may only indicate that a particular event has occurred in the DS or TS (if it is known at all and if the power supply has been affected) and announce the estimated time when the system will be operational. Each user shall ensure that all other users have obtained the information contained in this notification from the DSO, but may not pass on additional information other than as specified above.

- Information provision period

Information on upcoming activity will be submitted sufficiently in advance to allow the recipient to evaluate and assess attendant impacts and risks.

The notification shall be dictated to the recipient, who shall record it and repeat it to the sender, thereby checking that the notification has been recorded accurately.

- Requirements for information on incidents

A DS user shall inform the DSO of events in his system connected to the DS that has affected or could affect operation of the DS or TS.

The DSO shall inform the user of events in the DS or upon receipt of notifications on events in the TS that the DSO believes may have an operational effect on the user’s system connected to the DS. However, this does not prevent any of DS user from asking the DSO to provide information on events that have affected the DS user’s system.

Certain incidents may be brought about or exacerbated by other incidents or actions in the system of another party. In such case, the information reported will differ from information relating to an incident resulting from another incident or action.

The examples of situations listed below required the immediate transfer of information if they have an effect on operation, without limiting the general requirement for providing information in advance:

- the triggering of an alarm signal or an abnormal operational status signal;

- the occurrence of adverse weather conditions;

- the occurrence of malfunctions, errors, or temporarily limited functioning of equipment, including protective devices;

- increased risk of an emergency situation.

- Information format

The description of each event that occurs independently of another event or activity must be sufficiently detailed (even if the cause need not be specified) to enable the recipient to consider and assess the impacts and risks of the event. The recipient may raise questions relating to clarification of the notification.

Information that the DSO provides on an event caused by another event (the initial event) or an activity in a DS user’s system shall describe this event and contain information that the DSO has received from the DS user in relation to the initial event or activity. Such information shall be sufficiently detailed to enable the recipient to reasonably consider and assess the impacts and risks to the DS caused by the event and must contain a name with the clarification of the notification.

If a user submits a message on an activity or event in their system caused or affected by a random, proposed, or planned activity in someone else's system, their notification intended for the DSO shall contain the information that the user received on the activity. The DSO may pass this information on to other parties involved.

A user may only transfer information contained in the DSO’s notification to another subject connected to his system or to a system of another DSO if this is required by contractual conditions of connection in relation to an equivalent event in his system (if it was initiated or exacerbated by an event in the DS). Otherwise, users may not pass on any information contained in the notification from the DSO or notification from another user who received it from the DSO to any party connected to their systems. They may only indicate that a particular event has occurred in the DS or TS (if it is known at all and if it has affected the power supply) and announce the estimated time when the system will be operational.

With the exception of emergency situations, the notification shall be dictated to and recorded by the recipient and repeated to the sender. The sender shall check that the notification has been noted down accurately.

In cases where an electricity producer has notified the DSO of an event concerning the source, and if they need to more accurately assess the effect of this event on his system, they may request the DSO to provide detailed information on the parameters of the malfunction at the consumption point between the DS and the source at the time of this event. The DSO shall provide this information to the electricity producer as early as possible, provided that it is available.

- Information provision period

Information on occurrences shall be provided as soon as possible after their occurrence or at a time when the event is known or expected by the person making the notification.

- Serious incidents

In cases when an event in the DS or the DS user’s system has had or may have a significant effect on the system of any stakeholder, the operator of the relevant system will be notified in writing. Such an incident shall be referred to as a ‘serious incident’.

Without limiting the general description mentioned above, serious events shall include those that have or may have the following consequences:

- emergency operation of equipment, be it manual or automatic;

- voltage outside of the permitted range;

- grid frequency outside the permitted range, or system instability.

Central control conditions for the operator of the transmission system and distribution systems

The DSO’s central control – and in cooperation with the TS operator's central control, the TSO, and the DSO – must ensure all of its functions and activities have the highest degree of reliability attainable during operative control. To ensure its functionality and reliability, the DSO's central control utilises information from the TSO, the TSOCC-SCADA control and information system, electrical station control and information systems (CIS), SCADA production terminals, border terminals, and electrical station terminals.

The SCADA system provides enhanced support for fault resistance mechanisms. It is essential to make full use of the reliability support system:

- on-line switching of ‘hot – standby’ computer modes;

- computer connection via disc arrays with content mirroring;

- a redundant LAN with automatic switching to a second network in the event that errors or low network capacity are detected.

New SCADA equipment and connected equipment must use standardised STN EN 60870-5-101, STN EN 60870-5-104, and STN EN 61 850 protocols, with an effort to minimise the use of older proprietary protocols. Requirements for transmission routes are specified by the TSO and DSO in accordance with applicable telecommunications laws.

The electrical substation control and information system (ESCIS) must meet the requirements of the local information, control, and administrative system for the electrical substation and the requirements imposed on ESCIS by central control.

Installation of ESCIS is required in all new (newly built) electrical substations. ESCIS forms the core of the integrated electrical substation management technology and its concept is characterised by decentralised construction.

The purpose of installing automated or remotely controlled switching, measuring, monitoring elements is to ensure reliable and secure operation of the distribution system. Essential components include appropriate measuring, monitoring, protective and, in particular, communication equipment for optical networks, or global mobile communications networks, or radio communications. The criterion for choosing a particular element (technically, geographically) and the form of its communication with higher order control, operational, or measurement systems is the extent and frequency of the interaction required and its impact on enhancing safety and improving the level of global or local quality indicators.

Connections between central control systems and substations preferentially use independent power system telecommunications technologies (SCADA, ESCIS, ADR, optical fibre, SDH, PDH, RRL,...) owned by the subjects making the connections. Control systems and telecommunication equipment must be protected from unauthorised intervention, and security measures shall be hardware and software-based.

# Technical specifications for measurement in the distribution system

  - Control Centre metering

It is essential to establish technical conditions for central measurement and signalling in order to ensure reliable central control of the DS (in cooperation with TS and ES control as a whole). The technical specifications shall be understood as the minimum and shall be accepted and complied with by all DS users. Voltage measurement must be implemented for all three phases with a maximum error of 2 %, where each link in the measurement chain must have an accuracy of at least 1 %.

Current measurement must be implemented for all three phases with a maximum error of 2 %, where each link in the measurement chain must have an accuracy of at least 1 %. Measurement of the active and reactive power will be calculated from measured current and voltage values by the measuring equipment. The ranges of measurement transducers shall be consulted with the DSO.

State signalling for switching elements (circuit breaker, disconnector, grounding switch) must be two-bit (i.e. four-criteria). The signalling of malfunctions, protections, blockage states of switching elements and other operational signalling is single-bit (two-criteria).

Circuit breaker state signalling must be implemented for each outlet. A time stamp is required for all communicated quantities.

The DSO may stipulate other requirements for the accuracy of measurement and any network calculations in a special regulation.

Instrument transformers shall be installed in power line or transformer outlets in such a manner that the measurement function is not affected by the operation of power lines or the transformer through the busbar switch.

Local and remote measuring instruments shall be connected to a separate current transformer winding.

It is necessary to check the permissible voltage drop in the circuit of the secondary side of an instrument voltage transformer. The operating load of an instrument voltage transformer must be within the load range for which the accuracy class is guaranteed by the manufacturer.

The quality of input and output signals of measuring transducers and the transmission of the control parameters must correspond to the quality stipulated for on-line regulation circuits. Cycle accuracy and times may temporarily be inferior for existing equipment, but compliance with requirements is required for new equipment or upgrades of old equipment.

Conditions for installing commercial metering

Commercial metering is conducted for the purposes of stipulating payment for electricity that has been supplied, taken off or transmitted, for daily billing and for billing for distribution services. The legislative and content-related framework is provided by the relevant legislation. The conditions for installing commercial metering are laid down in the Operating Regulations.

# Technical specifications for the provision of universal service

Technical specifications for providing a metered service and the termination of the universal service are governed by the Operating Regulations.

# Technical specifications for interruption of electricity supply

  - Reasons for interruption or restriction of electricity supply from a technical perspective

The DSO may restrict or interrupt the supply of electrical energy without the right to compensation for losses from a technical perspective, especially in the following cases:

- an immediate threat to human life, health, or property and the elimination of these situations;

- states of emergency or when preventing a state of emergency;

- unauthorised use or supply of electricity;

- prevention of access to measuring equipment or a disconnect point (DP) by an electricity subscriber or producer;

- planned work on system facilities or in the buffer zone;

- faults in system facilities and during their elimination;

- delivery of electrical energy via facilities that are a threat to human life, health, or property;

- use of electrical energy by equipment that affects the quality and reliability of electrical energy delivery, if the subscriber does not take corrective measures using available technical means by the required due date after notification from the DSO;

- delivery of electrical energy by equipment that affects the quality and reliability of electrical energy delivery, if the producer does not take corrective measures using available technical means by the required due date after notification from the DSO;

- if the owner of equipment connected to the DS does not provide valid proof of the safety, reliability, and operability of equipment connected to the DS, for example a technical inspection and technical test report, an official equipment test, or LOR, even after being asked to do so in writing.

Reasons for interruption or restriction of production of electricity sources from a technical point of view

The DSO may restrict or interrupt the supply of electrical energy, especially in the following cases:

- an immediate threat to human life, health, or property and the elimination of these situations;

- states of emergency or when preventing a state of emergency;

- unauthorised use or supply of electricity;

- prevention of access to measuring equipment by the electricity producer;

- planned work on system facilities or in the buffer zone;

- faults in system facilities and during their elimination;

- delivery of electrical energy via facilities that are a threat to human life, health, or property;

- delivery of electrical energy by equipment that affects the quality and reliability of electrical energy delivery, if the producer does not take corrective measures using available technical means by the required due date after notification from the DSO;

- if the owner of equipment connected to the DS does not provide valid proof of the safety, reliability, and operability of equipment connected to the DS, for example a technical inspection and technical test report, an official equipment test, or LOR, even after being asked to do so in writing.

- in the event of failure to provide on-line data to central control, or providing erroneous data

During the course of planned work on system equipment or in the buffer zone, system equipment faults and during their elimination, as well as during changes to basic connections in the DS, the DSO has the right to restrict an electricity producer in two ways:

- by placing the relevant part of the DS into a zero-voltage condition;

- in the case of an electrical generation source that can be remotely controlled from the power distribution CC, by blocking the activation of the main disconnect point.

A producer must not in any way bypass the blockage of the generating plant and restore the generation of electricity during its blockage by the power distribution CC. Otherwise, the DSO will judge this as a serious breach of contractual conditions agreed upon by the DSO and the electricity producer.

Procedures for planned reconstruction and repair of distribution system installations

Repair and maintenance planning is the sum of the activities and technical organisational measures focusing on the reliable operation of the DS. The owner of the relevant installation is responsible for maintenance and repairs Maintenance work is divided into two categories: preventive maintenance and unplanned maintenance (fault elimination).

The purpose of planning repairs and maintenance is to define basic rules and identify the procedures for ensuring fault-free operation of DS facilities and define the legal authority and responsibilities of maintenance units.

Based on inspections and equipment faults found, an annual repair and maintenance plan is drawn up that takes into account the facility disconnection plan.

Maintenance is conducted on DS equipment in accordance with the ‘Electrical Distribution Equipment Maintenance Rules’ defined by the DSO.

Once the detected faults have been rectified, the record made of the relevant inspection shall be archived in accordance with the DSO’s internal regulation until the next inspection.

In accordance with the preventive maintenance plan, the DSO may change the mode of operation of the applicable part of the equipment while conducting work that requires parts of the equipment to be turned off. During planned work, power distribution may be restricted or interrupted in the given location in accordance with Act No 251/2012, on energy and amending certain acts.

During a change in the mode of operation of the relevant part of the DS during planned reconstruction and repairs at the LV level, such connection is considered a justified case for purposes for defining automatic disconnection of power in TN distribution circuit networks pursuant to STN 33 2000-4-41.

Intervals at which it is necessary to conduct individual inspections are given by equipment type and inspection type, and these deadlines are specified in the ‘Inspection and Maintenance Regulation’. In the case of new equipment, the ‘Electrical Distribution Equipment Maintenance Regulation’ shall be amended in accordance with the requirements and recommendations of the applicable manufacturer.

Planning and preparation for DS operation in a defined territory

Binding conditions and rules for the organisation of preparations of distribution system operation are stipulated in the Central Control Rules for the Control of the Electrification System of the Slovak Republic, in the DSO’s technical specifications, as well as in operating instructions regarding preparations for operation issued by the DSO.

The objective of the DSO’s preparations for operation is to lay a foundation for reliable and economic operation of the distribution system in connection with the Slovak Republic’s electrification system. During all phases of preparation of DS operation, pursuant to applicable legislation, optimum operating solutions are searched for, and the necessary space for maintenance, renewal, and development of electrical facilities is created.

Procedures, deadlines, and methods submitting a request for planned work on DS equipment take place pursuant to the DSO's Operating Instructions, which are binding for all electrical equipment operators and participants in the electricity market connected to the distribution system, are published on the DSO's website in the Legislation section (https://www.vsds.sk/edso/domov/technicke-info/dokumenty).

Pursuant to Act No 251/2012, on energy and on changes to some acts, the DSO has the right to ask participants in the electricity market for annual, monthly, weekly, and daily information needed to prepare and control system operation during all of its phases and to assess system operation.

Operators of electrical equipment connected to the DS are required each year, by 31 March of the relevant year, or at any time upon request during the year, to submit to the DSO a list of current contact information for all workers authorised to submit equipment shutdown orders, as well as contact information for workers who perform manipulation pursuant to applicable authorisation for this electrical equipment.

Notification of power interruption or restriction

The DSO shall announce the beginning of planned restriction or interruption of power supply, including its duration, in accordance with applicable legislation.

Procedure in the event of accidents and faults of DS facilities and the method of rectifying their consequences

During serious faults or breakdowns involving distribution system equipment, assigned authorised DSO employees and the grid user must proceed pursuant to the Management Plan. The priority of implementation of orders and individual steps is defined by the supreme control unit, which, pursuant to the Central Control Rules and written control instructions, has direct control of equipment affected by the fault state. If there is a threat of major physical damage, a threat to human health or life, or a risk due to delay, operators proceed pursuant to the LOR or pursuant to applicable written central control instructions.

Any unplanned work on distribution system equipment is permitted by the DSO’s central control only during the elimination of faults and breakdowns, or only during equipment status where there is an immediate threat of equipment breakdown or fault, or unplanned interruption of distribution due to the equipment’s poor technical condition.

When eliminating the results of breakdowns and faults, the DSO may change the way the relevant part of the DS operates. When eliminating the results of breakdowns and faults, power distribution may be restricted or interrupted in the given location in accordance with Act No 251/2012, on energy and amending certain acts.

During a change in the mode of operation of the relevant part of the DS due to breakdowns or faults at the LV level, such connection is considered a justified case for purposes for defining automatic disconnection of power in TN distribution circuit networks pursuant to STN 33 2000-4-41.

# Technical specifications for disconnection from the distribution system

  - Reasons for disconnection from the System relating to technical factors

A user who has been proven by the DSO to have violated stipulated technical parameters for operation of equipment connected to the DS – or if it has been proven by the DSO that their equipment has a negative effect on voltage quality in the DS to such an extent as limits stipulated in Chapter 2.2 of this document – must correct the situation or disconnect equipment causing these effects from the DS, either immediately or by a deadline agreed upon with the DSO.

A user who has been proven by the DSO to threaten the safety of distribution system operation or threaten power supply reliability must take corrective measures or disconnect equipment that causes these problems from the DS, either immediately or by a date specified after coming to an agreement with the DSO.

If the situation is not corrected within the agreed-upon period and their negative effect on the system, a threat to safety, or reliability of power supply still exists, such a user will be disconnected from the DS without the right to claim compensation.

Procedure in the event of non-compliance with safety and operating regulations

If breaches of safety and operating regulations are detected, the DSO and the parties involved shall take immediate measures to ensure prompt rectification of the situation.

The negotiation procedure and the responsibility of the participating parties is determined by applicable occupational health and safety legislation.

Technical procedure for disconnection from the distribution system

The DSO specifies the disconnection method for individual subjects in the distribution system individually, taking into account:

- the voltage level at which the disconnection is taking place;

- the range of options in the given part of the system;

- the type of intelligent power meter installed and its degree of functionality;

- the manner in which connected equipment operates;

- safety and health protection;

- prevention of any damage to property.

# Technical specifications for distribution system control

Binding rules for distribution system control are stipulated in the Central Control Rules for the Control of the Electrification System of the Slovak Republic.

  - Operational control of DS operation within a specified area

Operational control ensures continuous control of DS operation within the specified area and at VHV, HV, and LV levels of central control. It addresses the issue of immediate operating states of the entire controlled DS and its individual parts in order to implement objectives stipulated by operation preparation while simultaneously addressing the impact of unforeseeable events. Operative control of the DS utilises information from production and distribution equipment and DS user equipment, a central control system working in real time, protection plans, and daily preparation of DS user equipment.

From the perspective of operation, the following cases may occur:

- basic operation of the ES SR is synchronous, parallel with other electrification systems, regulation of frequency and outputs delivered among individual energy systems is governed by applicable recommendations within the scope of international cooperation;

- extraordinary operation of the ES SR is operation isolated from other power systems. In this case, the DSO’s CC regulates frequency to the stipulated level and ensures restoration of parallel cooperation pursuant to recommendations within the scope of international cooperation.

Regulation of voltage and reactive outputs in the ES SR and DS in a specified area

The breakdown of responsibilities in the voltage regulation process:

- the voltage level in the 400 and 220 kV systems is the responsibility of the TSO CC;

- the voltage level in the VHV system is the responsibility of the DSO CC in cooperation with the TSO CC;

- the voltage level in the HV and LV system is the responsibility of the DSO CC.

- relevant central control facilities ensure voltage levels:

  - through an operational service of controlled power equipment through direct or indirect control;

  - remote voltage regulation.

- The TSO CC performs required calculations to determine parameters for the optimum set of measures in the area of voltage regulation in 400 kV and 220 kV systems according to the following criteria:

  - reliable and safe operation of the ES SR;

  - achieving minimum active losses in 400 kV and 220 kV systems while adhering to rules of international cooperation when controlling voltage and reactive outputs;

  - agreements with electricity subscribers.

- The DSO CC designs voltage levels at 110 kV and HV supply points so that voltage supplied to users is as close to nominal as possible and does not exceed the permitted deviation pursuant to the relevant standard.

- the DSO CC manages HV voltage levels:

  - through automatic regulation of VHV/HV transformer taps

  - through remote regulation using an operative controlled power equipment service.

- the DSO CC manages LV voltage levels:

  - through the relevant DSO department. it is performed manually by switching HV/LV transformer taps based on measured and calculated values so that nominal voltage does not exceed the permitted deviation pursuant to the relevant standard.

Operative changes to the electrification system connection schema

The distribution system connection schema prescribed by the daily plan is binding for all voltage levels after taking into account conditions for the safety and reliability of the distribution system, and if needed also for the Slovak power grid.

Operative changes to the connection schema from the approved connection schema in the daily plan are performed by the operative service of the relevant central control facility in unavoidable cases. The operative unit of the relevant central control facility provides the necessary coordination of operative changes to the DS connection.

The TSO and DSO inform each other at the level of operative central control units regarding changes to connection of node systems.

The procedure for planning taking a DS user’s equipment out of operation and placing this equipment back into operation is as follows:

- planned equipment outages must be properly prepared in all phases of operation preparations. After taking into account safety, DS reliability, assuming no risk is posed to human life, health or property, and within the scope of its operational authority, the DSO CC may permit the shutdown of equipment without prior programme preparation, for work and repairs during fault elimination, as well as for extraordinary work when there is a danger due to delay or there is a health risk.

- prior to every planned shutdown of production equipment, or shutoff of equipment for work, the DS user who is responsible for the equipment's operation must ask the DSO CC to agree with the equipment being taken out of operation. Activity related to taking distribution equipment out of operation may begin only after approval by the relevant central control service.

- all new and rebuilt electrical equipment of a DS user connected to the DS is commissioned in cooperation with the supplier and operator pursuant to an operating test programme submitted by the investor . This programme is approved by the relevant DSO unit.

- the person listed in the test programme for the DS user is responsible for following the programme for the commissioning of the equipment as such.

A DS user’s equipment that has been commissioned is considered as having been taken over for central control only after:

- technical specifications for connection to the DS have been met;

- completion of all prescribed and agreed-upon operating tests;

- approval of LOR by the relevant DSO;

- all documentation required for central control of the facility has been delivered;

- the functionality of the telecommunications connection and information and control technologies has been verified, if these are present;

- the operator has declared the equipment is operable.

Steps for taking a DS user's equipment out of operation and placing this equipment back into operation

Operational manipulation is defined as activities that change the immediate connection status of power equipment or settings of power equipment.

A manipulation order from the operations service must be executed by operating staff without delay in accordance with safety regulations, the DSO TS, the OI, and the LOR. An order from the operations service is not executed if it is unclear or evidently incorrect, and its execution could lead to a threat to human health or life or to extensive damage. In this case the operating staff must notify the operations service of this fact and ask for an explanation. However, if the individual issuing the central control order insists it be executed despite this warning, the given order must be executed after the proper entries have been made in operating logs and on a recording device. This, however, does not apply to cases where human health and life are at risk. The individual that insists on execution of the order takes full responsibility for the consequences.

Personnel must not operate a DS user’s equipment without permission from the operations service of the relevant central control facility, especially as follows: make changes to connections, perform tests, or change protection and automated equipment settings, make changes in control and information system databases, and on other equipment that is under central control. This does not apply to exceptional cases where there is a threat of extensive damage, a threat to human health and life, and where delay poses a threat. Production or electrical station personnel shall immediately inform the relevant dispatcher of the activities in these exceptional cases.

Personnel manipulating a DS user’s equipment must repeat an order received from central control personnel prior to executing it.

When performing complex operating manipulations, a written procedure in the form of an M-order must be created in advance. An M-order does not have to be created:

- when performing manipulations for which procedures are stipulated in the LOR;

- when performing manipulations for which procedures are controlled or checked by CIS;

- during manipulations related to the elimination of fault states, where delay poses a threat.

Manipulations in a DS user’s substations are on principle performed ‘remotely’ from the appropriate central control facility or from control cabinets (feeder terminals) in the switchgear without unblocking. ‘Local’ manipulation with unblocking directly from the control cabinet is possible only with the approval of central control, and an M-order is issued for it, or if the manipulation is prepared in advance in the daily plan and an M-order approved by the relevant responsible employee of the given substation and central control is issued for it. This procedure may only be sidestepped in cases where there is a threat to human health or life, or extensive damage to equipment.

Manipulation that can be performed only during ‘unblocking’ must comply with LOR and must be approved by the appropriate central control facility. The employee performing the manipulation in the substation shall draw attention to this fact when they receive this manipulation order from central control, and shall confirm that all conditions have been met for LOR compliance.

For extraordinary manipulations that are performed during ‘unblocking’, manipulation breakdowns must be prepared in advance, specifying special safety measures.

In cases when a fault in the blocking system makes it necessary to perform manipulation locally during unblocking or directly using pneumatic valves, the operations service of the relevant central control facility, after considering the risks of the situation and risks of unblocked manipulation, shall decide:

- if manipulation will continue only once the fault in the blocking system is eliminated;

- if manipulation will continue with the blocking system out of service (unblocking).

In this absolutely exceptional case in a given substation, such manipulation must be performed by two individuals, one of which is a supervisor. The provisions of this point need not be complied with in the case of a threat to human health or life or extensive damage to equipment.

If more than one person is performing operating manipulation in a substation at the same time, one of them must be a supervisor. In this case the supervisor issues the employee performing the manipulation successive instructions for performance of the manipulation task, while checking the procedure is correct prior to the performance of the manipulation.

Prior to performing operating manipulation, the individual performing the manipulation must repeat the order to the ordering authority and then make a written record of the order. This record may replace that made by an automatic recording device.

Central control staff of central control facilities coordinate manipulations in individual substations while respecting worker safety and the needs of ES SR operation.

The central control service that issued the order to perform the relevant manipulation considers it to have been fulfilled in the following cases:

- after the individual who received the order notifies it that the requested manipulation has been performed;

- after remotely transmitted information via SCADA that the order was executed. In this case, however, this option must be specified in the LOR.

- Reconnection of a DS user’s specified equipment to the DS after a fault

When an operator of specified equipment requests reconnection to the DS after disconnection from the DS due to a fault involving damage to the equipment, fulfilment of obligations pursuant to § 35(2)(g) of Act No 251/2012, on energy, is considered to have been proven upon submission to the DS operator of a document regarding fulfilment of technical measures through diagnostics (measurement and tests) of the repaired equipment, made out by an authorised individual who confirms the equipment can be connected to the DS without affecting power distribution quality.

Work and records of work on a DS user’s electrical equipment

Work on equipment is considered to be tasks performed pursuant to applicable standards. Applicable safety regulations for operators and work on electrical equipment are mandatory for performance of this work.

Records of all work on VHV and HV equipment are the responsibility of licence holders administering the equipment, or who are authorised to operate the equipment based on authorisation agreements, or where operation is the responsibility of the applicable central control facility. In the case of other power equipment operators, the operating personnel of these power facilities are responsible (hereinafter ‘delegated substation’). Different cases must be specified in the LOR.

Work on released equipment is approved by the staff of the relevant central control facility or an authorised employee of the delegated substation based on information that the equipment has been switched off, disconnected, and grounded at all ends, including the entry of a ‘B’ order into operating records as specified by the DSO TS.

Operating records with ‘B’ order numbers must be kept at relevant central control facilities and other facilities in a clear manner in order to avoid erroneous record-keeping.

Work on equipment under voltage. This is a special work mode subject to approval by the appropriate central control level.

Responsibilities of shift personnel when on duty and during shift changes

Shift personnel in all power facility central control rooms and control room work according to approved shift schedules. Schedules are drawn up according to agreed-upon principles and are approved by workplace managers. Only workplace managers may make changes to shift staffing.

Each year, always by 31 March, and then always when a change occurs, the managers of all central control facilities and power facilities must exchange lists of names of employees who are involved with central control of the ES SR, giving their job position. The obligation to exchange this information applies to cooperating workplaces.

Shift changes are recorded in the operating log, where aside from information on the time and names of employees changing shifts, all routine and abnormal situations related to the activity of the relevant workplace must be recorded.

The transfer of a change service shall be prohibited in cases of:

- if the shift change could threaten human life, health, or safety;

- if there is a direct natural or other threat to the facility or equipment;

- if the new shift is insufficiently familiar with the status of the equipment they are assuming responsibility for and the issues involved, especially during the course of dealing with an outage or unfinished complex manipulation tasks;

- for other serious and urgent reasons, based on direct prohibition issued by the applicable workplace manager.

If the reasons for the shift change prohibition are long-term, the manager of the relevant workplace or other authorised employee will decide on rotation of operations personnel.

Principles for keeping service records for a DS user's electrical equipment

Service records are based on operating logs, used at all central control levels and by on-duty shifts of energy facilities. SCADA resources can be used to create an operating log.

At all of these workplaces, the operating log is used to record duty handover and acceptance, orders received and issued, and all operating events.

The following content is mandatory for keeping records in the operating log:

- the date and precise time of the report or order;

- the event location;

- a description of/command used for the event;

- report/command issued by – performed by;

- if the operating log permits, also information regarding who received the command.

Operating instructions, local operating regulations, and other binding documentation for central control

- Operating Instructions (OI)

These are an integral part of the MP, specifying its individual provisions as specialised work procedures and processes. They primarily address areas of activity that change over relatively short intervals. The OI are issued and approved according to job description. OI are issued after approval by the manager of the higher-order control facility. This ensures coordination and mutual cooperation between central control facilities in areas that are not contained in the Central Control Rules.

- Local Operating Regulations (LOR):

These clarify and supplement operating instructions, provide instructions to operating personnel of individual power or other facilities and specify work procedures and the technical description for the relevant power facility. They address issues that concern a limited number of workplaces. The LOR must not be at odds with the DSO’s management plan and technical specifications.

The approval process, marking and archiving shall be determined by the management of the operational units. This does not apply to provisions of this MP or OI that explicitly specify a different procedure.

Binding documentation (BD) for central control of the DS SR provides individual central control units the necessary information on the function and connection schema of individual pieces of power facility equipment, including SCADA equipment. Power facility operators must provide relevant central control facilities information to add to the BD in the required scope and quality and in a timely manner.

Instructions and control activities related to central control must be issued as an OI or through approval of LOR.

Principles of archiving central control documentation

Operations preparation materials are stored for 3 years.

The duty service operating log and other central control operating records and assessments, including fault analyses, are archived for 5 years.

The materials that are important for later processing are stored or systemically archived on the relevant department of dispatch control. These are primarily the following materials:

- basic schematics of the unified ES SR or part thereof;

- annual analyses (assessment of control room operations, including dates new power facilities and SCADA functions are put into operation).

If the aforementioned materials are used to document the progress of matters that require monitoring over a longer time period than relevant time spans, they are archived until the matter is completely and finally closed.

The specified archiving periods are minimum values.

# Technical specifications for SCADA, stipulation of requirements for the collection and delivery of information of central control of DS user equipment

  - Supervisory control and data acquisition for the ES (SCADA)

Control of operation of the DS SR takes place through a SCADA system. This is a continuous process of controlling the operation of individual facilities of the DS SR from relevant central control facilities.

SCADA must be implemented in all central control rooms and power facilities as a single functional whole on the controlling and controlled side. SCADA systems are built based on compatible hardware and software elements. Database connections between control levels are implemented by mutual agreement.

Any interference with SCADA functions that affect information and proof of DS SR operation or part thereof is forbidden without prior discussions with responsible employees of the relevant central control facility and on-duty central control personnel.

Central control facilities of all levels and selected control centres of power facilities (control rooms) must ensure continuous recording of all phone or radio phone orders and operations calls by on-duty central control personnel. This recording must be protected from damage and must contain a time signal.

Recordings are kept for:

- at least one month, as long as the recording does not contain records of a fault or other serious operation incident;

- three months, if the recording contains a record of a fault or other serious operation incident. If the fault or event analysis has not been closed, until its definitive closure.

Central control personnel and power facility operations personnel must make phone calls dealing with operations through phone facilities that have a functional recording device.

SCADA power supply equipment must rule out outages and no-voltage states.

New power facilities being commissioned must be equipped with SCADA devices pursuant to specifications defined by the appropriate DSO department.

Operation, maintenance, and inspections of SCADA devices is governed by the relevant OI. Maintenance activities must be included in the annual maintenance plan, which must be updated and clarified during all phases of operations preparation in connection with the annual maintenance plan for power devices in the ES SR.

The maintenance plan must include coordination with the maintenance of other areas that are part of or connect to SCADA devices of the DS SR.

Any reduction in reliability due to the performance of the above work must be approved by the relevant central control departments that this reliability reduction concerns.

# Technical specifications for stipulating technical safety criteria for the DS

  - Safety when working on distribution system facilities

Work safety rules for work on DS equipment serve to ensure work safety in the system, which the DSO shall apply in such a manner as to fulfil the requirements of the Energy Act and other statutory regulations and conditions within the scope of RONI authorisation for the distribution of electrical energy.

Users of the DS are required to comply with the same rules and standards for ensuring work safety while conducting work and testing at the consumption point between the DSO and the user.

The DSO and all users of the DS must comply with rules for ensuring work safety, including those who are in a mutual relationship with them, including:

- producers of electrical energy;

- other DSOs connected to this DS;

- subscribers at the VHV and HV voltage levels;

- any other party specified at the discretion of the DSO.

- Approved safety assurance systems

A work safety assurance system determines principles and procedures where it is necessary to have documentation that is used to ensure the protection of health and safety of all persons working on DS equipment or equipment connected to it, and where the responsibility of employees preparing and managing the work has been delineated. This system is specified by the DSO and other DS users specified in the DS OS.

In general, work safety is governed by applicable legislation, primarily the following:

- Act of the Slovak National Council No 124/2006, on occupational health and safety and amending certain acts;

- Ministry of Labour, Social Affairs, and Family of the Slovak Republic Decree No 508/2009, establishing details on ensuring occupational health and safety when working with pressure, lifting, electrical, and gas equipment, and stipulating equipment deemed to be specified equipment;

- Ministry of Labour, Social Affairs, and Family of the Slovak Republic Decree No 46/2010, stipulating details of ensuring occupational health and safety during forestry work and details on professional qualifications for the performance of some work activities and the operation of some equipment.

- Operating interfaces and principles

The locations of operating interfaces on which the safety management system must be based shall be determined by mutual agreement. The agreement shall also specify the persons in charge of the occupational safety assurance system.

The DSO and user shall maintain relevant documentation regarding occupational safety assurance.

This documentation shall contain records of the safety measures taken when:

- performing work on or testing of VHV and HV equipment in the DS and consumption points between the DS and users;

- disconnection or grounding of another system;

- Where appropriate, the DSO and the user shall exchange their occupational safety assurance regulations and any related documentation for each consumption point.

- Authorised personnel

The safety assurance system must contain provisions on written authorisation for employees who are involved with the administration, operation, work, or testing of equipment and devices that constitute part of the DS.

Each individual authorisation must specify the type of work it applies to and must precisely define the part of the system to which it applies.

Safety in managing the distribution system

Responsibility for the control of parts of the system is determined by agreement between the DSO and the user in accordance with the management plan for controlling the electrification system of the Slovak Republic (MP) and the DSO’s operating instructions.

This will ensure that there is always only one contracting party responsible for a particular part of a facility or equipment.

- Documentation

The DSO and the user shall document, by a method approved by the DSO, all applicable operational events that have transpired in the DS in any system connected to it, as well as the implementation of the safety regulations.

The DSO and the applicable user shall keep all documentation relating to the DS or the user’s system and to the implementation of safety measures or tests for the amount of time established by applicable regulations, but in any case for not less than one year.

- System schematics

The DSO and the applicable DS user shall exchange schematics that shall contain a sufficient amount of information to enable administrative personnel to fulfil their duties.

- Communication

Systems for communication between the DSO and users shall be established in places where the DSO specifies a commensurate need, so as to ensure workable, reliable, and safe control of the system.

In cases in which the DSO decides that backup or alternative communication systems are necessary for reliable and safe operation, the DSO shall agree with users upon these means as well as their implementation.

In order to ensure effective coordination of activities, the DSO and applicable users shall exchange a list of telephone numbers and call signs.

The DSO and the applicable users shall ensure that personnel with the necessary authorisation are continuously available at all locations where operations require them.

Construction safety

Measures must be taken to ensure the safety and protection of construction sites in accordance with statutory regulations and RONI authorisation.

All contracting parties shall take measures to ensure that construction personnel are warned of the specific risks of construction by suitable means before entering the construction site. This includes both temporary and permanent construction risks. Where there is a risk of contamination or similar risk, the personnel must be provided with appropriate personal protective equipment and procedures for eliminating any consequences of such risks must be ensured.

At construction sites with equipment installed that is the property of the DSO, inspection checks shall be carried out by management representatives and the DSO’s relevant occupational safety department.

Preventive fault propagation plan and restoration plan after a system outage

The preventive fault propagation plan and restoration plan after a system outage are the subject of an agreement between the DSO and TSO and are contained in special operating instructions (OI).

Limiting consumption in emergency situations

The operation regulations for the DS relate to measures for controlling consumption during emergency situations or during activities immediately preventing them from occurring. These measures are taken by the DSO or by a user with his own system connected to this DS pursuant to Act No 179/2011, on economic mobilisation and on changes and amendments to Act No 387/2002, on state governance during crisis situations outside of wartime conditions and during wartime conditions, as amended, and Slovak Ministry of the Economy Decree No 416/2012, establishing details on the procedure when declaring a state of emergency, on declaring limitation measures during a state of emergency, and on measures intended to rectify a state of emergency.

This part applies to:

- reducing consumption:

  - by reducing voltage;

  - by reducing the power used by selected consumers in accordance with the announced stage of the regulation plan;

- interruption of power distribution according to the cut-off plan, independent of network frequency;

- automatic frequency disconnection according to the frequency plan depending on the drop in network frequency.

The term ‘consumption management’ encompasses all of these methods, the purpose of which is to achieve a new balance between supply and demand.

The objective is to establish procedures enabling the LDSO to achieve a reduction in consumption in order to prevent fault inception or overloading of any part of the electrical system without causing impermissible discrimination against a customer or a group of customers. In doing so, the DSO shall follow the decree on emergency situations, the TS operating instructions and other regulations.

This part applies to the DSO and DS users. It does not apply to supply from the DS intended for nuclear sources. Consumption control carried out by the DSO may influence a local DSO connected to the DS in question, as well as its subscribers.

- Emergency measures procedure

Measures to reduce consumption within the DS:

- The DSO may make use of means to reduce consumption in order to prevent malfunctions from occurring or the system from becoming overloaded. The DSO is responsible for the use of these measures.

- The DSO shall draw up a consumption restriction plan, pursuant to Ministry of Economy of the Slovak Republic Decree No 416/2012, establishing details of the procedure when applying limitation measures during a state of emergency, and on measures intended to rectify a state of emergency in the power sector, and according to instructions from the TS operator’s central control.

The use of the consumption restriction plan is declared and rescinded by the TSOCC, and the DSOCC ensures its regulation pursuant to the decree.

- Automatic frequency disconnection according to the frequency plan

The DSO shall ensure the availability of technical means for automatic frequency disconnection at selected points of the DS in the event of a drop in system frequency below the value given by the frequency plan.

The frequency plan is created by the TSO CC in cooperation with the DSO’s relevant operation preparation units.

Automatic load switching shall be performed when the frequency falls below 49.0 Hz. The number of levels, their settings and the magnitude of the disconnection load shall be determined by DSO CC based on calculations. In the range of 49.0 to 48.1 Hz, frequency switching is used to address system failures, while switching to levels below 48.1 Hz can also be used for local malfunctions.

When choosing the disconnection load, the DSO shall take into consideration the safe operation of facilities and the risk of causing damage to affected customers.

- Informing users

If the DSO conducts consumption control according to the instructions or requirements of the TSOCC or TSO in order to protect the TS, they must react quickly and only afterwards provide users with information upon request by suitable means.

If the DSO conducts consumption control for the purpose of protecting the DS, they shall subsequently inform DS users by suitable means as needed upon request.

Distribution system operating conditions in emergency situations

This part of the DSO TS specifies procedures used after a total or partial shutdown of the DS confirmed by the DSO, who has announced that it will apply these procedures upon being notified.

The DSO is required to implement measures and procedures resulting from an emergency situation relating to his DS. This obligation arises from Act No 251/2012 on energy and amending certain acts. Details are stipulated by Ministry of Economy of the Slovak Republic Decree No 416/2012, establishing details on the procedure when implementing restrictions during a state of emergency, and on measures intended to rectify a state of emergency in the electrical power sector.

Details are stipulated by Ministry of Economy of the Slovak Republic Decree No 416/2012, establishing details on the procedure when implementing restrictions during a state of emergency, and on measures intended to rectify a state of emergency in the electrical power sector.

Measures for a state of emergency are coordinated with plans of operators of the TS, adjacent DS and other important partners. Limitations in the electrical power sector are applied as:

- a consumption limitation plan,

- an emergency disconnection plan,

- a frequency disconnection plan.

Distribution system tests

This part of the DSO TS stipulates duties and procedures during the organisation and performance of tests on the DS that have or may have a significant impact on the DS or users’ systems. These are tests in which irregular, unusual or extreme conditions in the DS or a part of the DS, in a neighbouring DS and in the TS are simulated or triggered in a controlled manner. Tests during commissioning of facilities and/or repeated tests shall not be included in this category of tests.

The goal of this section is to ensure that procedures used in the organisation and performance of tests on the DS do not present a risk to the safety of employees or the public and to ensure that they present the lowest risk possible to the distribution of electrical energy, the source, or equipment, and that they do not have a negative effect on the DSO and users. It establishes the procedures to be followed when preparing and reporting tests in the DS.

This section relates to the DSO, its customers on the VHV and HV network, electrical energy producers and local DS operators.

In general, a test on the DS proposed by the DSO or a user connected to the DS that may also affect the TS must be in compliance with the technical specifications for transmission system operation and the technical specifications for distribution system operation.

Minimal impact on the TS is deemed to include deviations in voltage, frequency, and shape of the sine wave not exceeding the permissible deviations specified in applicable TSO documents.

Issues regarding testing of equipment in the DS are stipulated in the OI in the Substantive Plan and Schedule (SPS), which is issued by a DSO department and is published on the company’s website.

- Information on proposed tests

If the DSO or a user intends to conduct a test of their system that will or could affect an outside network, they shall notify those who could be affected by the test.

The proposal shall be made in writing - in printed or electronic form - and shall contain information on the nature and purpose of the proposed test on the DS, as well as on the power and location of the applicable source or equipment.

If the recipient of the proposal considers the information insufficient, it shall request additional information from the proposing party (also in writing).

- Testing schedule

The proposing party shall provide the other concerned parties with information about the final schedule of the DS test by no later than one month before the date of the test. The schedule shall indicate the sequence, anticipated disconnection time and the personnel conducting the test, including persons responsible for occupational safety, and other facts deemed necessary.

The coordinator must be informed without delay and in writing of any problems connected with the test of the DS that may arise or that are anticipated from the time the programme is issued until test execution.

If the operating conditions in the DS on the day of the proposed test are such that any of the participating parties wishes to delay or cancel the commencement or continuation of the test, this party shall immediately inform the coordinator of its decision and reasons. Depending on the circumstances of the test, the coordinator shall then cancel or postpone the test and, if possible, agree upon another suitable date with the participating parties.

- Final report

After the DS test has been completed, the proposing party shall be responsible for drawing up a written (final) report on the test, which shall be presented to all participating parties.

This final report shall contain a description of the machinery or installation that has been tested and a description of the test performed, including the results, conclusions and recommendations.

Development and renewal of the distribution system

Pursuant to Act No 251/2012, on energy and amending certain acts, the DSO is responsible for maintaining reliable and safe distribution system operation. In order to carry out these tasks, the DSO shall, among other things, ensure the planning and performance of repairs and maintenance of facilities and draw up a fault propagation prevention plan, as well as a plan for the development of the DS according to load and production forecasts. The assessment of needs for capital investment into the renewal of existing distribution system equipment also plays an important role in DS development planning. For this reason, DS development is also directly related to the subject of distribution system renewal in connection with ensuring safe and reliable DS operation in the future.

The obligation to ensure equipment maintenance and renewal also applies to system users - owners and operators of power facilities that have a direct effect on DS reliability and safety. Network users are also obliged to plan and announce an equipment shutoff request to the specified unit of the DSO - the Department of DS Operations Planning, and are obliged to provide all information necessary DS development planning.

DS development planning is a continuous activity resulting in the assurance of its reliable operation. In terms of time, DS development planning is divided into:

- long-term development with a timespan of 5 to 10 years and more;

- mid-term development with a timespan of up to 5 years;

- short-term development with a time horizon of up to 2 years.

The long-term development of the system is planned conceptually. The concept of long-term development and renewal of DS equipment is created at the level of individual equipment classes. It usually defines a DS development and renewal funding allocation framework for individual voltage levels.

Mid-term network development is based on long-term development and primarily specifies network development and renewal objectives at the VHV level with regards to specific investment intent.

Short-term network development is based on long-term and mid-term planning, and specifies network development and renewal objectives at the HV and LV level with regards to specific investment intent.

- Fundamental distribution system development planning documents

A network development study is fundamental to the DS development process. It further elaborates the plans and objectives of the DSO and specifies the measures and means for achieving them. It provides input for the transmission system development programme.

The study deals with the following areas:

- developing a DS configuration that meets expected power consumption growth; it respects the development aims of the TS and of power producers, the supply requirements of direct consumers, and international cooperation requirements;

- renewal of equipment that has reached the end of its service life based on operating parameter growth, short-circuit current growth, and equipment obsolescence;

- ensuring distribution services with regard to reliability, stability of operational parameters and streamlining and modernisation of technological and operating activities.

The instrument for addressing DS development and analysing individual network modes is a mathematical model of the DS prepared primarily for the long-term development timespan.

The projected load of transformations from the DS to the TS and to other DS in individual nodes for a 10-year development outlook and under the conditions of a basic connection on the consumption side is established on the basis of data from the development units of each DS. The data may be revised on the basis of macroeconomic studies of national economic development with respect to regional development, economic sectors and their energy consumption and demographic indicators. The balances are determined from the measurement of the winter peak of the year in question.

The planned degree of load development in the DS usually takes into account the average year-over-year growth in power consumption in the SR specified in the TS Development Ten-Year Plan.

- Relationships between the distribution system and its users

Close cooperation between the DSO and its users is necessary when planning development, especially transformation from the DS to the lower-voltage distribution networks when assessing the issue of running power from new electrical energy sources as well as when resolving problems of a local nature. Close cooperation is primarily required with the holders of RONI authorisation for the production and distribution of electrical energy to which network calculations relate to the greatest extent.

- Relationships between the distribution and transmission system

The development of the DS must also be coordinated with the development of connected DS and TS. The objective of the study is to define optimum distribution system development and renewal in order to ensure fulfilment of the legislative and normative framework. The study takes into account development and renewal of TS elements.

- Input data for distribution system development studies

The development of DS power lines shall be based on the results of an analysis of existing and, above all, prospective conditions in the DS. It is based on real-life load data, information regarding projected load and consumption trends, information on existing equipment in the area, and statistical data on existing and future elements of the TS and interacting systems.

The operators of the DS and TS shall mutually exchange data needed for network calculations of established network operation, short-circuit calculations, and dynamic system behaviour calculations for time spans that are usually of 5 and 10 years.

The network balance model for maximum load calculations is based on results of systematic measurement of the DS (also taking into account maximum loading and the differential discrepancy between intermediate or minimum loading); for HV and LV models, it is based on appropriately chosen statistical load values. Evaluation of the transmission and voltage relationships at minimum system loading is based on summer measurements.

In designing the development of transformation between the TS and DS, competent bodies exchange data regarding the projected power supply and demand balance at individual nodes. With regard to sources, this concerns the location and available capacity of power plants supplying the DS. In the area of consumption, this is the loading of transformers from the TS to the DS (MW and MVAr) at individual nodes. Data exchange takes place each year by a specified date and in a form that has been mutually agreed upon.

The exchanged data may not be used for purposes other than conceptual work or made available to a third party without the consent of the party which provided the data.

ANNEX 1

The quality of electricity in the distribution system and its evaluation

Contents

1.	In general	38

2.	Voltage characteristics in the distribution system	38

3.	Voltage characteristics of electricity supplied to the DS by sources	39

4.	Power quality parameter evaluation methods	39

# In general

Quality of electricity is one of the quality standards used during the distribution of electricity. It is defined as a set of selected voltage characteristics at a given point in the DS under normal operating conditions, compared with limit or with informative reference technical parameter values. These characteristics do not apply to abnormal operating conditions, including:

- temporary power arrangements to ensure the continuity of electricity supply to grid users under conditions that occur due to a fault, maintenance and construction work, or to minimise the extent and duration of power outages;

- cases when a system user’s installation or equipment fails to meet relevant standards or technical specifications for connection stipulated by the DSO, including limit values of conducted interference;

- abnormal situations (extreme weather conditions, natural disasters, acts of third parties, orders from state administration authorities, force majeure, and during insufficient power due to external circumstances).

Voltage characteristics for which limit values are specified are characterised by a persistent phenomenon, i.e. discrepancies from rated value that are permanent over time. Such a phenomenon occurs mainly due to load characteristics, load changes, or due to non-linear loads.

Voltage characteristics for which only informative values are specified are characterised by voltage events, i.e. sudden and significant deviations from the normal and required waveform. Voltage events usually occur due to unpredictable circumstances (for example faults) or external circumstances (weather conditions or activities of a third party). Only indicative values are specified for these characteristics, not limit values.

# Voltage characteristics in the distribution system

The voltage level in the VHV system is given by the agreed-upon voltage Uc. If the voltage value is not contractually agreed upon, in general the nominal voltage for a three-phase VHV system is Un=110 kV line to line.

The nominal voltage for a three-phase HV system is Un=22 kV and Un=10 kV line to line.

The normalised nominal voltage for the public four-wire three-phase LV system is Un=230 V line to neutral.

Individual voltage characteristics describing power quality for these voltage levels are based on the current version of the STN EN 50160 technical standard.

The technical standard defines the following guaranteed characteristics for persistent phenomena:

- system frequency;

- supply voltage deviations;

- rapid voltage changes (a single rapid change, the degree of flicker perception);

- supply voltage asymmetry;

- harmonic voltage components;

- interharmonic voltage components;

- the level of signal voltages in the network.

Characteristics with informational value only:

- supply voltage interruptions;

- supply voltage dips;

- supply voltage increases;

- transient overvoltage (generally caused by lightning, or due to switching in the network).

The required levels of individual parameters for consumers in LV networks is defined for the interface between DS equipment and the user’s equipment. All guaranteed voltage characteristics must be in compliance with the requirement of standard STN EN 50160.

Voltage-related events (voltage dips, voltage increases, and voltage interruptions) are, due to their nature, very unpredictable and change based on their location and time of occurrence. The STN EN 50160 standard provides only indicative values for these characteristics.

# Voltage characteristics of electricity supplied to the DS by sources

For electricity supplied to the DS by power generating facilities, certain quality parameters also apply at the common connection point, like the requirements specified for power consumption - defined in detail in Chapter 2.2 of the main document.

# Power quality parameter evaluation methods

The procedures defined in technical standards STN EN 61000-4-30, STN EN 61000-4-7, STN EN 61000-4-15, and STN EN 50160 provide a foundation for measuring and evaluating voltage characteristics; these standards also define requirements for measuring sets that guarantee measurement repeatability.

When measuring voltage characteristics, it is necessary to measure and evaluate those voltages to which consumption and sources are connected, i.e. in four-wire LV networks, it is necessary to evaluate the voltage between the phases and the neutral conductor. In three-wire HV and VHV networks, phase to phase voltage must be evaluated.

Voltage characteristics with indicative values are monitored and evaluated according to expected values specified by the standard.

ANNEX 2

Instrumentation requirements

Contents

1.	Instrument transformers	41

2.	Signalling	41

# Instrument transformers

Accuracy class of current and voltage instrument transformers:

- 0.2s for current transformers used for commercial metering at the VHV level;

- 0.5s for current transformers used for commercial metering at the HV and LV level;

- 0.2 for voltage transformers used for commercial metering at the VHV level;

- 0.5 for voltage transformers used for commercial metering at the VHV level;

- 0.5 % for central control measurements;

- 0.5 % for informative measurements;

- 5P10 for current transformers used for electrical protection functionality;

- 3P for voltage transformers used for electrical protection functionality.

Secondary outputs:

- MTP – 1 (5) A

- MTN – 100, 100/√3 , 100/3 V

# Signalling

The transmission and processing of a signal in one direction, or a command in the opposite direction in the following chain: technology – CIS of the controlled object — transmission – SCADA of the DSO’s control centre (time from contact closure in the equipment after the signal has been displayed on the monitor) < 5 s

Reaction time of the CIS-controlled object (time from contact closure in the equipment after the signal has been sent to the communication line) << 1 s

Analogous reaction time of the DSO CC SCADA system (time from when the command is sent on the monitor to when the signal has been sent to the communication line) << 1 s

ANNEX 3

Rules for connection of sources and electricity storage facilities to the DS

Contents

1.	PURPOSE	44

2.	BASIC TERMS AND ABBREVIATIONS	44

2.1	Basic terms and definitions	44

2.2	Abbreviations	45

3.	CONNECTION CONCEPTS	46

3.1	Property boundaries	46

3.2	Standard methods of connection to the DS	46

3.2.1	Standard method of connection to the LV system	46

3.2.2	Standard method of connection to the HV network	50

3.2.3	Standard method of connection to the VHV network	51

3.3	Connection of a source to third-party electrical equipment	52

3.4	Hybrid LV systems	53

4.	REQUIREMENTS FOR POWER GENERATION EQUIPMENT	54

4.1	Switching equipment	55

4.1.1	A disconnect point - DP (permanently accessible switching equipment):	55

4.1.2	Main isolation point – MIP (coupling switch)	55

4.2	Network protection	56

4.2.1	Required configuration of network protection for disconnecting generating equipment from the DS for types A, B, C and D	56

4.2.2	Required configuration of network protection for reconnection of a source following a planned shutdown or fault in the DS	60

4.3	Requirements for the operation or instrumentation of sources for types A, B, C and D	61

4.3.1	Frequency stability of sources – requirements for types A, B, C and D	61

4.3.2	Rate of change of frequency (RoCoF) – requirements for types A,B,C and D	61

4.3.3	Activation of active power reduction in the event of over-frequency (LFSM-O) – requirement for types A, B, C and D		61

4.3.4	Permissible reduction of active power during a frequency decrease –requirement for types A, B, C and D	62

4.3.5	Restoration of active power after a fault – requirement for synchronous units of types B, C and D	62

4.3.6	Restoration of active power after a fault – requirement for asynchronous units types B, C and D	62

4.3.7	Operational capability during a short-circuit – requirement for types B and C	62

4.3.8	Operational capability during a short-circuit – requirement for type D	64

4.3.9	Voltage ranges – requirement for type D	66

4.3.10	Requirements for stabilisation feedback after a fault – requirement for type D synchronous units	66

4.3.11	Island operation – requirement for type C and D sources	66

4.3.12	Loss of angular stability – requirement for types C and D	66

4.3.13	Quick re-synchronisation/transfer to own consumption – requirement for types C and D	66

4.3.14	Settings of synchronisation devices – type D requirement	67

4.3.15	Black start – requirement for types C and D	67

4.3.16	Period to reach the adjusted active power output set-point – requirement for types C and D	67

4.3.17	Activation of active power output increase during under-frequency (LFSM-U) – requirement for types C and D		67

4.3.18	Active power response to a change in frequency FSM – requirement for types C and D	68

4.3.19	Frequency restoration control – requirement for types C and D	68

4.3.20	Active power change rate – requirement for types C and D	68

4.3.21	Prioritisation of the active or reactive power contribution – requirement for type C and D asynchronous units		68

4.3.22	Power oscillation damping – requirement for type C and D asynchronous units	68

4.3.23	Instrumentation/damping of power oscillations – requirement for type C and D sources	68

4.3.24	Simulation models – requirement for types C and D	69

4.3.25	Monitoring of active power response to frequency changes – requirement for types C and D	69

4.3.26	Requirements for reactive power for synchronous units on types C and D	69

4.3.27	Reactive power requirements for asynchronous units of types C and D	70

4.4	Installations with reactive power regulation, requirements for reactive power of sources	72

4.5	Devices with non-regulable/non-configurable reactive power	73

5.	ELECTRICITY METERS, METERING AND CONTROL EQUIPMENT	74

5.1	Situation of metering devices	75

5.2	Requirements for cooperation with control and information systems	75

6.	CONNECTION SPECIFICATIONS	77

6.1	Voltage increase	78

6.2	Connection of synchronous generators	80

6.3	Connection of asynchronous generators	80

6.4	Connection of sources with inverters, with frequency changers	80

6.5	Connection of sources to the 110 kV network	80

6.6	Connection checks for cumulative power	80

7.	BACK EFFECTS ON THE DISTRIBUTION SYSTEM	81

8.	SOURCE COMMISSIONING	81

8.1	Local operation regulations, technical inspection	81

8.2	Functional tests	83

8.3	Approval of permanent source operation	84

9.	SOURCE OPERATION	85

# PURPOSE

The technical specifications in this Annex apply to all electricity generating installations to be connected and operated in parallel with the DS in the territory of Východoslovenská distribučná a. s. These specifications must be used for all new construction and reconstruction, and increases or decreases to the total installed or achievable output of existing power plants. For electricity storage (accumulation) facilities, in discharge mode, i.e. supplying power to the DS, or supplying a DS user’s electrical equipment, the technical specifications for a power generating installation shall apply.

# BASIC TERMS AND ABBREVIATIONS

  - Basic terms and definitions

A facility for the generation of electricity (hereinafter a ‘source’) is defined pursuant to Act No 251/2012, the Energy Act, as a facility for generating electricity that serves to transform various sources of energy to electricity; it includes a structural part and equipment. The source represents the part of the customer’s facility in which one or more generators are located, including all equipment necessary for their operation. Formulae (the mathematical relationships listed below) relating to the source contain the subscript ‘A’.

A source location, for purposes of connection to the DS, is also defined as a place (a property, grounds, or area on which the structural and technological parts of the source are situated) belonging to one source connection applicant, which is a separate spatially or territorially enclosed, permanently electrically connected whole, and which is equipped with a specified measuring instrument.

A connection point is the point of contact between the DS and the DS user’s equipment where electricity enters or exits the DS. A connection point is usually the property line between the DSO’s equipment and the user’s equipment.

A common supply point or a common connection point is the nearest point of the distribution system into which source output is supplied, and to which other subscribers or sources are or can be connected.

A power plant block is a part of the source consisting of one generator including all equipment necessary for its operation. The boundary of the power plant block is the location where it is connected to other blocks or to the DS. Formulae (the mathematical relationships listed below) relating to one power plant block contain the subscript ‘E’.

A generator is part of the power plant block including an inverter (for example in the case of a photovoltaic power plant) but not including capacitors if they are used for power factor compensation. The transformer adapting the generator’s voltage to the voltage of the DS is also not considered part of the generator. Formulae (the mathematical relationships listed below) relating to one generator contain the subscript ‘G’.

Flicker is a subjective perception of changes in light output.

Harmonics are sine waves with frequencies that are integral multiples of the fundamental frequency (50 Hz).

Interharmonics are sine waves with frequencies that are not integral multiples of the fundamental frequency (50 Hz). Note: Inter-harmonics may also occur in the frequency range between 0 and 50 Hz.

Reclosing is the closing of a breaker circuit, connected to a part of the network in which a fault exists, by an automatic device after a time interval, permitting a transient fault to be eliminated from this part of the network.

An inverter is a device for converting direct current into alternating current and vice versa. The installed power of the inverter shall be considered to be the achievable continuous output power of the inverter on the AC voltage side.

Inverters controlled by their own frequency do not need any outside voltage for commutation, but for parallel operation with the network they need to derive trigger impulse control from the network frequency. They are capable of island operation if they have an internal reference frequency and additional regulation for sustained island operation, which they transfer into by either automatic or manual switching in the event of a failure.

Network-controlled inverters need outside voltage for commutation that is not part of the inverter’s source. Such inverters are not capable of island operation as defined by these specifications.

Total installed active source output is the electrical output a generator is capable of producing under normal operating conditions, for which it has been designed, and the value of which is stated on its nameplate or in documentation issued by the generator’s manufacturer (rated generator output). The total active installed output of a photovoltaic power plant is the sum of the outputs of photovoltaic panels, given in Wp. The total active installed output of a power plant with rotary generators is the sum of installed outputs of its generator(s). Achievable source output is the maximum value of electrical output that the source is capable of producing under conditions that are limited by specific operating parameters of its design.

The total installed capacity of an electricity storage (accumulation) device is given by the sum of installed capacities of the inverter of this device on the AC side. Where a power storage facility is part of a source and uses common inverters to convert direct current, the installed power of such equipment shall be determined as the higher of the sum of the installed power of the inverters and the total installed power of the sources. In other cases, the installed capacity of such equipment is determined by the sum of installed power inverters of electricity storage facilities and the installed source power capacities.

  - Abbreviations

LSE	Local source of electricity

SSE	small source of electricity.

Plt, Alt	long-term degree of flicker perception; long-term flicker interference factor; flicker perception level Plt over a duration of 2 h (lt = long time). Note: Plt=0.46 is the stipulated maximum interference value for one source. The value of Plt may be measured and evaluated with a flicker meter. Aside from the flicker perception level Plt, a flicker interference factor Alt is also used, where the relationship between the two is Alt = Plt3.

PN 		Total active installed output of the source

S kV 		short-circuit output at a common supply point

ykV 		short-circuit impedance phase angle

Un		rated system voltage

ΔU	voltage change; the difference between the effective value at the beginning of the voltage change and the resulting effective values. Note: The relative change Δu refers to the voltage change of the combined voltage ΔU relative to grid voltage Un. If the voltage change ΔU has the meaning of phase voltage loss, then the relative voltage change applies Δu = ΔU/Un/√(3).

c	equipment flicker coefficient; a dimensionless parameter specific to the given equipment, which, together with two characteristic parameters (equipment output and short-circuit output at the common supply point) determines the magnitude of flicker caused by the equipment at the common supply point. The standard distinguishes between the flicker coefficient for steady operation (wind energy plants), which depends on the network’s internal short-circuit impedance angle, and the flicker coefficient for connection and disconnection switching.

SA		the rated apparent output of a source

SAmax		the maximum apparent output of a source

S nE 		the rated apparent output of a power plant block

SnG		the nominal apparent output of a generator

ji 		the phase angle of own source current

cos j		cosine of phase angle between fundamental harmonic voltage and current

- true power factor – the ratio of active and imaginary power

k 		the ratio between the starting or inrush current and the nominal current of a generator

Ia		starting current

Ir		the current for which a source is dimensioned (usually nominal current In)

kk1		short-circuit ratio, the ratio between SkV and the maximum apparent output of a source SrAmax

# CONNECTION CONCEPTS

Standard solutions for connecting sources to the DS and definitions of terms for electrical connections for sources (the beginning and end of the connection) are analogous to definitions for consumption equipment specified in the Energy Act, as amended, unless specified otherwise in this document.

For parallel operation of generating equipment with the DS, we discern:

- 'On-grid' systems – these are governed by and dependent on the DS frequency. In the case of an outage in the DS they are incapable of operation, and in the case of PVPS the inverter is switched off. The system can only be restarted once power has been restored in the DS (when voltage and frequency values in the DS are both within prescribed values for the amount of time specified by the DSO).

- 'Hybrid' systems (also called 'off-grid' systems) – a hybrid system works in parallel with the DS and is only temporarily powered by the DS, preferably when it is producing no power. Hybrid systems must meet VSD's technical specifications and commercial terms and conditions (Distribution System Operator Technical Specifications, Distribution System Operator Operating Regulations) and technical specifications for connection.

The conditions for their connection and parallel operation with DS are set out in Chapter 3.4.

  - Property boundaries

Property boundaries are specified in parts of the standard connection method according to the relevant voltage level.

Standard methods of connection to the DS

The objective for implementation of a connection to the DS is to minimize costs while complying with all conditions during later operation of the DS. When designing the connection point and method, it is necessary to respect the type and method of operation of the source itself, as well as network conditions in the given area of the DS. The information provided specifies the minimum output size from which it is necessary to connect the source to the HV or VHV network, and the maximum output up to which it is possible to connect to the LV or HV network.

Any connection of a source to the DS is implemented through a switching device that simultaneously functions as a separation element between the source and network facilities. This switching device must be as close as possible to the branching-off point and always accessible to DSO employees.

The DSO decides how the source will be connected to the DS. The standard connection of one source to the DS is a connection to one point in the DS. A separate consumption point for powering the internal consumption of a source is not a standard solution for sources with installed output up to 1 MW.

Standard method of connection to the LV system

The method of connection to the LV network is selected based on primarily the following criteria:

- method of source operation (entire production to the DS/excess production to DS);

- technical suitability and financial demands of the connection.

If the source is to supply excess power to the DS, an A1 connection is selected (this solution can be used for residences only if the internal needs of the source will not be covered by power from the DS).

TS

MS

Source

MIP

Connection point

LV

TS

MS

Source

MIP

Consumption

Connection point

LV

Property boundary

Property boundary

A1.	A2.

LV

Connection point

MS2

MS1

Source

TS

Property boundary

MIP

Consumption

A3

Figure 1: Connection of a power generator to the LV network - connection to LV lines

If the source is to supply its entire production to the DS, either an A2 connection is selected if a separate connection has been built for the source, or if the installed output of the source is ≤ 30 kW/connection point and there is an existing connection to the LV network (a home connection, etc.), an A3 connection can be used (for example, due to significant technical difficulty and the cost of an A2 solution compared to A3). For an A3 solution, the use of a connection cabinet with two sets of breakers is suitable. If such a connection point is not technically suitable, the building's connection must be built (another connection point — A2), or modified by the applicant.

The ownership boundary for the source operator's electrical equipment is the termination of the LV conductor (supply line) connected to the connection or disconnect cabinet (cable network) owned by the DSO.

Connection point

Property boundary

MIP

Source

MS

DP

HV

LV

Outputs

TS

A4.

Figure 2: Connection of a power source to the LV network – separate output in a transformer substation (TS)

where:

CC - connection cabinet/disconnect cabinet (usually performs the function of a DP);

MS - meter switchboard;

DP - disconnect point (a publicly accessible switching point with a disconnect function);

MIP - main isolation point (coupling switch);

TS – transformer substation

Informative LV connection power limits (based on source connectivity calculation) that can be adjusted depending on the specific connection point to DS:

- up to and including 4.6 kW of installed capacity - power supplied in a single phase can also be considered, with direct connection to the home circuits or the use of an existing connection or separate LV connection to the DS.

- above 4.6 kW and at the same time up to and including 30 kW of installed power - it is possible to consider delivering the power three-phase with direct connection to the domestic wiring using the existing connection if the calculation of the connection of the source confirms this, or by a separate LV connection to the DS.

- over 30 kW of installed power supply — it is possible to consider transferring the power to the distribution HV/LV TS to the LV side of the substation switchboard, or it is necessary to adjust the DS or the electrical connection, where the total installed power of the sources shall not exceed 80 % of the installed power of the transformer. In this case, an A4 connection is selected, where the power supply is connected to the power switching and circuit breakers in the LV switchboard. The property boundary between the source operator’s electrical devices is the end of the LV cable connected to the LV switchboard of the substation (such as a solution using loop terminals). In this case a three-phase connection of the source is chosen on principle.

In the case of an existing connection to the DS, the following also applies (an existing LV connection):

- the original property boundary does not change if the branch-off from the DS, the connection cabinet and lines between the CC and MS or from the switchboard breaker cabinet remain original, unless specified otherwise in applicable planning, construction, and reconstruction principles for LV and HV Networks of the DSO, or in the applicable electrical distribution equipment maintenance rules.

- The DSO has the right to request that metering be situated in a publicly accessible location (in the sense of a standard method of connection to the LV network) if the connection of the source requires reconstruction of the electrical connection or supply lines, or of relevant breaker and disconnect cabinets, or metering switchboards.

A5.

Figure 3: Connection of a source to the LV network in the common areas of an apartment building

| Bytový rozvádzač | Apartment switchboard |
| --- | --- |
| Zdroj | Source |
| Istič | Breaker |
| Istič/HRM | Breaker/MIP |
| Vývodový istič /RM/ | Output breaker (DP) |
| Elektromer | Electricity meter |
| Hlavný istič | Main breaker |
| Stúpacie vedenie bytového domu /HDV/ | Apartment building power riser (MBW) |
| Hranica majeku | Property boundary |

For connection of a small source in an apartment building, general requirements for metering modification apply. The output breaker in the main building wiring (MBW) cabinet must be located near the electricity meter. In this case, the disconnect point (DP) is the output breaker past the electricity meter and the main isolation point (MIP) is a separate breaker for protecting the source in the apartment switchboard (Diagram A5). The MIP may also be located outside the incoming apartment switchboard only if this is the only source past the electricity meter. The connection between the MBW junction box and the main breaker, the main breaker and the electricity meter, and the electricity meter with the output breaker, including a PEN conductor, must consist of a solid copper conductor with PVC insulation or a braided copper conductor with PVC insulation, terminated with crimp sleeves.

The minimum interior space for situating an electricity meter and communications unit with sufficient room for manipulation is specified in the ‘Electricity Metering Specifications’ on the DSO’s website. Housings of uninsulated unmetered parts must be prepared for sealing. The main breaker (before the meter) and the output breaker (past the meter) must be visible and permanently marked.

Standard method of connection to the HV network

A connection to the HV network may be implemented as follows:

- by connecting the source to the HV distribution line

In the case of connection to the HV distribution line, the source operator shall establish his own substation at a location near the HV line agreed upon with the DSO. The substation will be connected to the DS:

- either via an overhead HV line by branching off from a support point - an outdoor T connection according to Diagram B1. The connection length should be minimised. For branching off, the DSO prefers the use of a vertical section disconnect switch owned by the DSO along the route of existing HV lines with disconnect point (DP) functionality. The design of the section disconnect switch must permit the installation of a short circuiting kit to safeguard the HV connection to the source.

- or with an HV cable, when preference is given to connecting the cable to a free HV connection at a nearby distribution substation owned by the DSO (Diagram B2), or a connection with the cable entering an outdoor HV switchboard with a disconnect switch past the T-connection owned by the DSO, which will be built above the cable route and will perform the function of a disconnect point (DP) with the DS.

A cable connection of a source by looping a substation not owned by the DSO is not a standard connection.

Connection point

HV

Property boundary

HV

DP

DSO TS

TS

Property boundary

DP

Altern. 1

MIP

TS

TS

Property boundary

DP

MS

Altern. 1

Altern. 1

MIP

MIP

HV

Altern. 2

MIP

LV

DS

LV

Altern. 2

MIP

Altern. 2

MIP

Source

Source

Source

B1.	B2.	B3.

Figure 4: Connection of a source of electricity to the HV network

- connection of a source to an HV switchboard of a VHV/HV substation

If the type and operation of a source, as well as the network conditions in the relevant part of the DS, require power to be taken off from the source and fed directly into an HV switchboard of a VHV/HV substation or an HV switching station, solution B3 is selected. The applicant for connection shall set up a transfer station at a location agreed upon with the DSO. They shall install an HV line from the transfer station location connected to the substation, and connect it to an existing feeder bay. The switch bay for the output line is specified on the basis of the specific prerequisites of the existing DS and the equipment design (single- or multi-system distribution points) in such a manner that future operation will be simple and clear. For one source, one bay in the HV substation or HV switching station switchboard is reserved (DS conditions permitting).

In the case of a B1 connection (outdoor connection), the property boundary of the source operator’s electrical facility is the end of the anchor strap on the switching element towards the source on the overhead HV line, or the cable terminals of the connection on the pole on which the section disconnect switching element is installed (see Chapter 4.1). For connection of a cable to the outdoor HV switchboard with a disconnect past the T-connection, which will be built above the cable route and will function as a disconnect point for the power plant with the DS, the aforementioned HV switchboard will be the property of the DSO, and the property boundary will be the cable terminals of the cable from the planned source substation terminated at this HV switchboard.

For B2 and B3 connections, property boundary for the source operator’s electrical facilities are the terminals of the HV cable entering the HV/LV or VHV/HV substation or switching station.

Standard method of connection to the VHV network

The source operator shall establish his own 110 kV/HV substation at a location agreed upon with the DSO. In principle, the substation may be connected to the VHV network as follows:

- by connecting the source to a bay on a VHV switchboard of a VHV/HV substation

The source operator shall install a VHV line connected to his own electrical substation (ES) and connect it to an existing feeder bay of the DSO’s substation in accordance with C1. The feeder bay for power output is specified on the basis of the specific prerequisites of the existing network and equipment design (dual- or multi-system switchboard) facilitating simple and clear future operation.

- by looping an existing VHV line to the source operator’s substation

In case of wiring according to Diagram C2, the construction of the power station of the source operator (H type or incomplete H type) is subject to the least possible distance from the existing VHV line. The situation of metering equipment for connections C1 and C2 (similarly as for B2 and B3) is addressed individually depending on the connection point, specific circumstances, and source size.

DSO ES

Transfer station

Source

Property boundary

VHV

VHV

Property boundary

C1.	C2.

Figure 5: Connection of a source of electricity to the VHV network

The property line in Figure 5 is indicated by a dotted line. If there is no VHV feeder array and it needs to be set up in an existing station for purposes of connecting the source (Diagram C1), the DSO will own this feeder array in the DSO ES. The method for connecting the substation to the VHV network, as well as the substation type, can also differ in justified cases. This is possible only following DSO approval.

Connection of a source to third-party electrical equipment

Connection of a source to equipment not owned by the DSO (third-party electrical equipment) is contingent on the written consent of the owner of the electrical equipment for connection of the source to his equipment. In this case, the existing property boundary and resultant responsibility for the operation of this equipment does not change. The owner of the electrical equipment to which the source is connected must, prior to connection, submit in writing all documents required by applicable legislation to confirm safe and reliable operation of electrical equipment connected to the DS.

Connection of a source to third-party electrical equipment must not result in transit metering of electricity. Transit metering is defined as billing metering devices being arranged in series. Connecting a source to third-party electrical equipment is not cause for changes to the location of existing electricity metering unless the DSO decides otherwise.

Connection of multiple sources to third-party electrical equipment (Diagram D2) without submitting ‘Certification of Compliance of Planned Investment with Long-Term Energy Policy’ (hereinafter ‘certification’) is possible only when the installed output of the source(s) of identical type is less than the value stipulated in the current Energy Act. The criterion for stipulating installed output of a source is the value of total installed output of generator(s) of identical type. Otherwise, certification needs to be submitted.

Connection point

Connection point

HV

Property boundary

DP

Property boundary

HV

DP

third-party TS

Altern. 1

MIP

MS

third-party TS

MS

MS

LV

MIP

MIP

MIP

Altern. 2

Source

Source

Source

Source

D1.	D2.

Figure 6: Connection of a source to third-party electrical equipment

Hybrid LV systems

Hybrid systems are generating plants that are capable of operating in parallel with the DS as well as of island (off-grid) operation if they have an internal reference frequency and additional regulation, or suitable production/consumption separation for temporary island operation, which they transfer into by either automatic or manual switching in the event of a DS outage. For temporary island operation, they either use energy obtained from the generator or energy stored in various ways that permit its use at any time. When switching to temporary island operation, a hybrid system must disconnect the relevant installation from the DS in all phases according to the connection method.

Connection of a 1-phase hybrid system to an existing 3-phase supply point installation is contingent on the output from the system (inverter) not being connected to 3-phase loads, but rather to the common input to single-phase breakers for outlet circuits. A 1-phase hybrid power supply can back up or power only single-phase circuits, not three-phase appliances. Only hybrid systems that are approved by VSD, a.s. and their system connection method and used elements (system hardware and software equipment) in the installation meet the requirements for connection and operation in DS.

- Fundamental requirements for hybrid LV systems:

Generator – the equipment must have its MRC approved for the entire installed output (in the case of a solar power plant, this is the sum of the outputs of solar panels).

MIP – connects the entire consumption point or part thereof from the DS, so in the case of island operation, electrical equipment must not consume/supply electricity from/to the DS via the MIP, i.e. the MIP contacts must be open. The mere installation of devices regulating output, for example reverse power protection, a power router, or similar devices that declare ‘zero’ supply to the billing meter is not a sufficient technical solution. Consumption equipment can only be split into a part backed up by a hybrid system and a non-backed up part in that part of the installation that is located between the source and the MIP. The MIP may be part of other equipment (for example an inverter) only if it meets the DSO’s technical requirements during type testing performed by the DSO.

Network protection – gives a command to the MIP to reconnect (engage MIP contacts) the source in parallel with the DS only if DS parameters (U and f) are within the prescribed range for the amount of time the DSO prescribes to the source operator in its statement. Reconnection to the DS outside the aforementioned case is forbidden!

The MIP contains network protection that can be configured according to DSO requirements. Approved types of hybrid systems, including the approved way of engaging them, are listed on the DSO website (https://www.vsds.sk/edso/domov/vyrobcovia-elektriny/pripojenie-zdroja/hybrid). Technical information and documents. Aside from the above requirements, a hybrid system must also comply with all requirements for systems not capable of temporary island operation. If a single-phase hybrid system is installed, it can be backed up by or power only single-phase circuits and appliances.

For hybrid systems, integrated network protection and a switching element (MIP) can be used only if compliance with the DSO's technical specifications is demonstrably achieved during physical type testing of the system, and simultaneously the installation to which the hybrid system will be connected can be reliably and safely split into backed-up and non-backed-up sections.

# REQUIREMENTS FOR POWER GENERATION EQUIPMENT

Only such equipment whose feedback does not negatively affect the DS and its users by exceeding permitted parameter values for electrical energy, pursuant to Chapter 6 of this Annex, may be connected to the DSO's grid. The method and location of the connection are determined by the DSO, taking into account given system conditions, the type, output, and mode of operation of the source, as well as the source operator’s rightful interests. This should guarantee that the source will be operated without causing interference and will not endanger other equipment connected to the DS.

A basic prerequisite for connecting a source to the DS is prevention of introduction of back voltage into the network, and ensuring disconnection of the source from the DS if DS voltage is lower than the activation threshold of undervoltage protection (even in case of an outage on only one phase). For connection, either a coupling switch can be used that connects the entire facility (e.g. consumption as well as generation) to the DS, or a switch that connects the generator or multiple parallel generators with other equipment connected at the same connection point (with consumption). Activation of this coupling switch must be blocked until each phase has the required minimum voltage for undervoltage protection activation. Basically, a time delay of tens of seconds to several minutes between voltage restoration in the DS and connection of the source serves to protect the source itself.

During the construction, reconstruction, and operation of a source, it is necessary to heed the applicable ordinances and regulations, especially from the perspective of parallel operation with the DS, and in order to eliminate detrimental back effects on the DS or equipment of other consumers.

The following regulations must be complied with during the construction, reconstruction, and operation of electrical equipment:

- currently applicable laws and implementing legislation;

- applicable EN, STN, and PNE standards and/or the DSO’s operating standards;

- employee protection and occupational safety regulations;

- DSO Technical Specifications, DSO Operating Regulations, DSO orders and guidelines;

- the Management Plan.

In order to ensure sufficient sizing of equipment, in each case the short-circuit conditions at the connection point must be calculated and the short-circuit contribution of the source itself must be taken into account. The equipment’s short-circuit resistance must be greater than or at least equal to the greatest calculated total short-circuit current.

  - Switching equipment

From the perspective of the DSO’s interests and of safe and reliable DS operation, each source must contain primarily the following switching equipment:

A disconnect point - DP (permanently accessible switching equipment):

This is a publicly accessible switching point with disconnection (decoupling) functionality for purposes of visible disconnection of the user’s electrical equipment from the DS:

- in the LV network, a junction box or a distribution breaker cabinet can perform the function of visible switching equipment if it is permanently accessible without restriction (see Figure 1);

- in the LV network, an LV switching feeder element in the switchgear of an HV/LV substation (a fuse or fuse switch-disconnector) can be considered a permanently accessible switching element (see Figure 2) also because only one source is fed out. An LV circuit breaker doesn’t meet the requirements for visible disconnection, and thus cannot be considered a DP, which is why reconstruction is required when a source is connected.

- in an HV network, a section disconnector or decoupler owned by the DSO or by a third party (existing consumption points) can be considered a permanently accessible switching device (see Figure 4) if it is permanently publicly accessible to DSO employees for manipulation. The switching element will be transferred to the ownership of the DSO, or if it is in unsatisfactory technical condition, it will be replaced with a switching element owned by the DSO.

- in the case of sources with multiple generators, one common permanently accessible switching device must be used.

- if a source is connected in an apartment building, the feeder circuit breaker behind the electricity meter can be considered a DS (see Figure 3).

A switch used to connect a source to the DS serves as a permanently accessible switching point. Switch configuration depends on the connection, ownership, and operational conditions at the supply station. The DSO will stipulate more detailed information by prescribing technical specifications and business terms and conditions. The disconnect point should be owned by the DSO.

Main isolation point – MIP (coupling switch)

To connect a source to the DS, it is necessary to use a coupling switch that can, at minimum, switch off the load (a disconnect switch) and is preceded by short-circuit protection. This coupling switch – the main isolation point – may on the LV, HV, or VHV side. If island operation is not expected, this element can be considered the generator’s switching device. The switching device must ensure galvanic separation for all three phases. If required by the DSO, the MIP or another disconnect point should be remotely controlled. The DSO has the right to specify which switching elements will have a seal. In the case of one source with multiple generators, one common MIP will be used. The use of more than one MIP is regulated in Chapter 2.3 of the main part of the DSO TS.

Note: A relatively serious consequence of combining the function of separating the source from the network during DS malfunctions and during work on a connection line or identification of malfunctions, in the case of a simple connection, is the loss of power for internal consumption and resulting adverse effects when putting it back into operation. For this reason, it is better for a source connected in this way to give priority to turning off the generator and power for internal consumption once the drop in voltage has ended or after a successful source protection cycle remains available.

For equipment capable of island operation, a switch intended for synchronisation (usually represented by the MIP of the source, or by a separate device located between the disconnect point DP and the MIP of the source, or between the MIP and the source) is used to switch it off, which may occur due to the activity of protective devices during phenomena elicited in the DSO’s network. The function of a coupling connector and disconnector intended for synchronisation must be specified as part of the technical specifications for source connection.

An outage of auxiliary power for protective devices and switching devices must automatically lead to the source being switched off. For sources using an inverter, the switch must be located on the AC side of the inverter. If co-located in the inverter cabinet, the switching equipment may not be put out of operation by a short circuit in the inverter.

For photovoltaic sources with total installed output up to 11 kW, or 16 A per phase (small sources of electricity - SSE), with only one inverter that permits voltage and frequency protection to be configured according to DSO requirements, a switching element located on the AC side of the inverter covered to the inverter’s integrated protection can be considered an MIP. For hybrid (off-grid) systems, integrated network protection and a switching element can be used only if compliance with the DSO’s technical specifications is demonstrably achieved during physical type testing of the system.

If safety fuses are used as short-circuit protection with LV generators, it is necessary to size the switching equipment at least according to the cut-off range of current-limiting fuses.

The DSO will provide the source operator a short-circuit contribution from the network to the connection point. If the source increased short-circuit conditions in the DS above values for which network equipment is designed, the source operator must implement measures that limit short circuit current, or rather its effects, unless a different agreement is reached with the DSO.

The time graduation when connecting multiple generators at one common delivery point (common connection point) needs to be agreed with the DSO. Disconnection of the MIP should not restrict the source’s own consumption, except for sources capable of island operation.

  - Network protection

To ensure reliable and safe operation of the DS, the DSO and the power plant operator shall agree on a protection system, disconnect times, and protection selectivity and sensitivity. In the case of sources capable of island operation, protection must be ensured even during island operation. Source protection measures (e.g. short-circuit protection, overload protection, hazardous contact protection) must be implemented pursuant to STN 33 3051.

### Required configuration of network protection for disconnecting generating equipment from the DS for types A, B, C and D

In general it is necessary to use protection with the following functions depending on the type of generating equipment (the output limits of individual types of sources are specified in Chapter 2.3 of this document); the DSO may change the voltage settings for type A and B sources depending on the specific installation:

- Protection configuration requirements – disconnection of type A sources from the DS, including sources with active installed output up to 800 W

| Configuration of protection for type A sources including sources with PN up to 800 W, with voltage monitoring on the LV (Uf – phase voltage)/HV (Un – line voltage) side; |  |  |  |
| --- | --- | --- | --- |
| Function | Designation | Required setting |  |
|  |  | setting for disconnection | Max. disconnect time tmax (s) |
| Overvoltage | U> | 1.1 Uf/Un | 0.1 |
| Undervoltage | U< | 0.85 Uf/Un | 0.1 |
| Over-frequency | f> | 51.5 Hz | 0.1 |
| Under-frequency | f< | 47.5 Hz | 0.1 |

Table 1: Protection settings for disconnecting Type A sources, including those with PN up to 800 W from the DS

- Required protection settings – disconnection of type B sources from the DS

| Settings for type B source protection with voltage monitoring on the LV (Uf – phase voltage)/HV (Un – line voltage) side; |  |  |  |
| --- | --- | --- | --- |
| Function | Designation | Required setting |  |
|  |  | setting for disconnection | Max. disconnect time tmax (s) |
| Overvoltage - level 1 | U> | 1.1 Uf/Un | 0.5 |
| Overvoltage - level 2 | U>> | 1.2 Uf/Un | 0.1 |
| Undervoltage - level 1 | U< | 0.9 Uf/Un | 0.5 |
| Undervoltage - level 2 | U<< | 0.7 Uf/Un | 0.1 |
| Over-frequency | f> | 51.5 Hz | 0.1 |
| Under-frequency | f< | 47.5 Hz | 0.1 |

Table 2: Protection settings for disconnection of type B sources from the DS

- Required protection settings – disconnection of type C sources from the DS

Pursuant to Article 15.3 of Commission Regulation (EU) 2016/631 - with regards to voltage stability, type C sources must have automatic disconnection capability if the voltage at the connection point is out of the stipulated range. In general, it is necessary to use protection devices acting on the MIP with the following functions, with the protection times provided being maximum values, allowing the source to operate during a short-circuit according to the required voltage level over time pursuant to Article 14.3 of Commission Regulation (EU) 2016/631:

| Protection settings for type C sources |  |  |  |
| --- | --- | --- | --- |
| Function | setting range | Required setting |  |
|  |  | setting for disconnection | max. disconnect time tmax (s) |
| Undervoltage - level 1 U< | 0.10-1.0 Un | 0.85 Un | 2.7 s |
| Undervoltage - level 2 U<< | 0.10-1.0 Un | 0.3 Un | 0.35 s |
| Overvoltage - level 1 U> | 1.0 – 1.2 Un | 1.15 Un | 5 s |
| Overvoltage - level 2 U>> | 1.0 – 1.2 Un | 1.2 Un | Immediate |
| Over-frequency | 51.5 Hz | - | 0.1 |
| Under-frequency | 47.5 Hz | - | 0.1 |

Table 3: Required protection settings for type C sources – disconnection from the DS

- Required protection settings – disconnection of type D sources from the DS

Pursuant to Article 16.2(c) of Commission Regulation (EU) 2016/631 - with regards to voltage stability, type D sources must have automatic disconnection capability if the voltage at the connection point is out of the stipulated range. In general, it is necessary to use protections acting on the MIP with the following functionalities; the protection times provided are maximum values.

| Protection settings for type D sources connected to 110 kV (DS) |  |  |  |
| --- | --- | --- | --- |
| Function | setting range | Required setting |  |
|  |  | setting for disconnection | max. disconnection time |
| Undervoltage - level 1 U< | 0.10-1.0 Un | 0.85 Un | 2.7 s |
| Undervoltage - level 2 U<< | 0.10-1.0 Un | 0.3 Un | 0.35 s |
| Overvoltage - level 1 U> | 1.0 – 1.2 Un | 1.118 – 1.15 Un | 60 min |
| Overvoltage - level 2 U>> | 1.0 – 1.2 Un | > 1.15 Un | 5 s |
| Over-frequency | 51.5 Hz | - | 0.1 s |
| Under-frequency | 47.5 Hz | - | 0.1 s |

Table 4: Required protection settings for type D sources - disconnection from the DS

- Protection configuration requirements for type C and D sources

Power-generating units of 5 MVA and higher usually function in a block with a transformer, a transformer for own consumption, and an exciter. Such an arrangement must have protection as specified in Table 5:

| Protection | Electrical equipment |  |  |  |
| --- | --- | --- | --- | --- |
|  | Generator | Block transformer | Tap-changing transformer | Exciter |
| Differential short-circuit | N,3 | N | N | N |
| Distance short-circuit | N | - | N | N |
| Overcurrent short-circuit | N | - | - | - |
| Excitation loss | N | - | - | - |
| Anti-asynchronous operation | D | - | - | - |
| Asymmetry | N | - | - | - |
| Overload | N | - | N,4 | N |
| Reverse power | N | - | - | - |
| Stator earth fault | N | - | - | N |
| Coil | N,1 | - | - | - |
| Voltage | N,2 | - | - | - |
| Bearing currents | N | - | - | - |
| Frequency | N | - | - | - |
| Frame leakage | - | N | - | - |
| Gas relay | - | N | N | - |
| Rotor earth fault | N | - | - | N |

Table 5: Protection configuration requirements for type C and D sources

Table legend:

N – protection necessary;

D – protection recommended;

1 – for alternator stator parallel branches;

2 – two protective devices (mutual back-up);

3 – two protective devices for block and generator (mutual back-up);

4 – before and after the transformer.

To ensure stability in the DS, every source over 5 MVA must have the following automation installed:

- restoration;

- disconnect failure;

- remote shutdown switch;

- protective device connection path switching;

- output regulation switching from change in frequency;

- for remote output regulation;

- for remote voltage regulation;

- for ensuring transfer to own consumption during breakdown frequencies.

The DSO has the right to stipulate different protection settings for the source operator if required by DS or source operation. The DSO also has the right to ask an operator of an SSE to provide active response to changes in active power or to changes in frequency pursuant to STN EN 50 438, or currently applicable operating instructions from the TSO.

In four-wire LV networks, voltage settings apply to the voltage between the phases and the neutral conductor (so-called phase voltage). In three-wire HV and VHV networks, voltage settings apply to phase-to-phase (line) voltage.

In some cases, other protection settings may be necessary due to network conditions. For this reason, their settings must always be submitted to the DSO for approval. A connection feasibility study (back effects, dynamic behaviour of sources in the given network, etc.) may also serve as a foundation for these settings.

When switching off asynchronous generators, it is necessary to first disconnect compensation capacitors for reasons of protection from generator self-excitation and reverse voltage

Overvoltage and undervoltage protection must respect the number of phases of the source; for three-phase systems, it must be three-phase. Voltage monitoring must be three-phase in order to also be able to detect single-pole drops in voltage with certainty.

According to where the billing meter is situated, network protection monitors voltage on the LV side for sources with total installed output up to 100 kW (type A sources) and on the HV side for sources over 100 kW (type B, C and D sources connected to the DS).

Undervoltage and overvoltage protection switching times must be short (approx. 100 ms), so that rapid changes in voltage will not damage the equipment of other consumers or source equipment. In the event of self-excitation of an asynchronous generator, the applied voltage may reach such a high value during several cycles that damage to operating equipment cannot be ruled out.

With immediate disconnection of the source during source protection, synchronous generators are protected from activation in the antiphase upon automatic reactivation after a zero-voltage pause. Source protection is also only ensured when the network is not being supplied due to the zero-voltage pause. For this reason, the total of the switch-off time of the protective device and the actual switching time must be selected so that the zero-voltage pause during source protection will not be shortened significantly.

Protective devices for immediate shutdown during source protection (a vector step change and output relay, or directional excess overcurrent protection) are no substitute for the required voltage and frequency protection. Their settings must take into consideration the reaction to source load fluctuation and temporary effects in the network. With equipment capable of island operation, their main function is to detect island operation (with part of the DS), turn off the coupling disconnector, and thus prevent subsequent connection of the island network and the DS. It is necessary to coordinate the switch-off times of these protective devices with the corresponding voltage and frequency relay times.

Installation of a directional ground fault relay may be required to circumscribe part of the facility with a ground connection. This relay should only be engaged on signal.

Following connection of sources to the DS that are operated with source protection that could be jeopardised by the sources, delayed shutoff is permissible only if special protection is available for immediate source disconnection with source protection.

It is necessary to establish an interface (such as a terminal board with longitudinal division and test terminals) to conduct functional protection tests.

The source operator must themselves ensure that switching, voltage fluctuation, short-term interference such as source protection, or other transient phenomena in the DS do not damage their equipment. The DSO has the right to specify which protective devices will be sealed. For sources connected in the past with narrower voltage and frequency ranges configured, a change can be made to the source’s network protection settings pursuant to the data provided in the table providing network protection settings for the relevant power source type, based on a request from the source operator. Costs incurred by the DSO due to this change are borne by the subject making the request.

Photovoltaic sources with only one inverter that permits voltage and frequency protection to be configured according to DSO requirements do not require separate network protection.

### Required configuration of network protection for reconnection of a source following a planned shutdown or fault in the DS

Prior to reconnection to the DS, source equipment measures whether network voltage and network frequency are in the range given by the table for the appropriate source type specified in Table 6 and Table 7 below, depending on the reason for disconnection of the source from the DS.

Following repeated disconnection (shutdown), the source operator must notify the DSO.

- Automatic connection capability following planned disconnection – requirement for types A, B and C

After planned disconnection from the network, type A, B and C sources can be reconnected to the distribution system after the following criteria have been met:

- After receiving the signal to unblock the main disconnect point (hereinafter the MDP) from the DSO's control centre or automatically with a 300 – 900 s delay, depending on the source type.

- In light of established DS operation procedures, the DSO recommends setting the time lag for Type A sources at ‘300 s’ and for type 'B, C, D’ sources at ‘900 s’. These times reflect the typical time lag for performing manipulations when defining the fault point in the DS.

- The synchronising element can be switched on once voltage and frequency are within the stipulated range:

| Type A source |  | Type B, C source |  |
| --- | --- | --- | --- |
| Voltage at the connection point | 0.95 – 1.1 Uf /Un | Voltage at the connection point | 0.95 – 1.05 Uf /UN |
| Frequency range | 47.5 – 50.05 Hz | Frequency range | 47.5 – 50.05 Hz |
| Delay | 300 – 900 s | Delay | 300 – 900 s |

Table 6 Conditions for automatic connection of a source following planned disconnection

- The maximum permitted active power rate of increase at the output must be at most 10 % of PN per minute.

Type A sources for which network protection does not allow different settings for disconnection and connection are reconnected to the DS according to specifications for disconnection from the DS (Table 1: Protection settings for disconnection of Type A power supplies, including PN up to 800 W from the DS).

- The ability to automatically reconnect after a system fault – requirement for types B, C and D

Type B, C and D sources disconnected from the network due to the operation of protective devices on the MDP can be reconnected to the distribution system once the following criteria have been met:

- the synchronising element can be switched on once voltage and frequency have been within the stipulated range for 300 s:

| Type B, C or D source connected to the DS |  |
| --- | --- |
| Voltage at the connection point | 0.95 – 1.1 UN |
| Frequency range | 47.5 – 50.05 Hz |
| Delay | 300 – 900 s, |
| After receiving the signal to unlock the MDP from the DSO’s control centre or automatically with a 300 – 900 s delay |  |

Table 7 Conditions for automatic connection of a source following a fault

- the maximum permitted active power rate of increase at the output must be at most 10 % of PN per minute.

Type A sources disconnected from the network due to the operation of protective devices due to a fault in the system are connected according to the connection procedure after planned disconnection.

Requirements for the operation or instrumentation of sources for types A, B, C and D

### Frequency stability of sources – requirements for types A, B, C and D

Pursuant to Article 13.1(a) of Commission Regulation (EU) 2016/631, sources connected to the DS must be kept in operation depending on frequency as follows:

| Frequency range [Hz] | Required time period of operation [s] |
| --- | --- |
| 49 Hz (incl.) — 51 Hz (incl.) | time-unlimited operation |
| 47.5 Hz (inclusive) – 49 Hz | time-limited operation – at least 30 minutes |
| 51 Hz — 51.5 Hz | time-limited operation – at least 30 minutes |

Table 8: Required type A, B, C and D source frequency stability

### Rate of change of frequency (RoCoF) – requirements for types A,B,C and D

Pursuant to Article 13.1(b) of Commission Regulation (EU) 2016/631 - as regards the ability of the source to remain connected at a certain rate of change of frequency, the source must not disconnect if the RoCoF of the system is up to ±2 Hz/s, with RoCoF being measured as the mean value of the frequency derivative over 500 ms.

### Activation of active power reduction in the event of over-frequency (LFSM-O) – requirement for types A, B, C and D

Pursuant to Article 13.2 of Commission Regulation (EU) 2016/631 - in the event of Limited Frequency System Mode response for Overfrequency (LFSM-O), in order to minimise impact on adjacent areas, the following requirements apply to activation of reduction of active power during overfrequency:

- the frequency threshold for activation of change in active power output – 50.2 Hz;

- droop 5 %;

- the first reaction of the facility to frequency change is required within a maximum of 2 seconds. Later activation of active power output must be technically justified by the facility owner to the TSO;

- once the total active power reserve has been activated, the equipment shall remain at the minimum possible power.

### Permissible reduction of active power during a frequency decrease –requirement for types A, B, C and D

Pursuant to Article 13.4 and 13.5 of Commission Regulation (EU) 2016/631 - in justified cases, taking into account the technical capability of sources, the following active power reduction is permitted during decreasing frequency:

- frequency-dependent power reduction is not possible at system frequencies equal to or greater than 49 Hz;

- if network frequency drops below 49 Hz, active power can be reduced by up to 2 % PMAX/Hz;

- active power can be reduced during a frequency reduction only for generation facilities that are technically limited in this manner.

The active power reduction during a frequency reduction must be as small as possible given the technical capacities of the facility.

These reductions apply for the following ambient conditions:

- temperature 15 °C,

- relative humidity 60 %,

- elevation: 350-420 m asl

If the source is being operated under different conditions, its operator must provide the TSO with the correlation between ambient conditions and the change in the rate of decline of active power.

### Restoration of active power after a fault – requirement for synchronous units of types B, C and D

Pursuant to Article 17.3 of Commission Regulation (EU) 2016/631 - type B, C and D synchronous generation sources must be capable of restoring power after a fault within 150 ms of the incidence of the fault to the pre-fault value with a permitted gradient of 20 % of the pre-fault PN per second.

### Restoration of active power after a fault – requirement for asynchronous units types B, C and D

Pursuant to Article 20.3 of Commission Regulation (EU) 2016/631 - type B, C and D asynchronous generation sources must be capable of restoring power after a fault to 90 % of 'Ppre-fault' within 1 s of when 85 % of the 'Upre-fault' value is reached. The permitted deviation in delivered active power is 10 % of the 'Ppre-fault' value.

### Operational capability during a short-circuit – requirement for types B and C

Pursuant to Article 14.3 of Commission Regulation (EU) 2016/631 – with regard to the capability of a source to operate during a short-circuit (fault ride-through – FRT), during the voltage level duration defined below at the connection point for fault conditions, sources must be capable of maintaining their connection to the network and stable operation.

Synchronous Sources:

| t [s] | U [pu] |
| --- | --- |
| 0 – 0.15 | 0.05 |
| 0.15 | 0.7 |
| 1.5 | 0.85 |

Table 9: Requirements for operation during a short-circuit – type B and C synchronous sources

Figure 7: Requirements for operation during a short-circuit – type B and C synchronous sources

Asynchronous sources:

| t [s] | U [pu] |
| --- | --- |
| 0.15 | 0.05 |
| 0.15 | 0.15 |
| 3 | 0.85 |

Table 10: Requirements for operation during a short-circuit – type B and C asynchronous sources

Figure 8: Requirements for operation during a short-circuit – type B and C asynchronous sources

In case of asymmetrical faults, the same curves as for symmetrical faults shall apply.

### Operational capability during a short-circuit – requirement for type D

Pursuant to Article 16.3 of Commission Regulation (EU) 2016/631 - with regards to the capability of a source to operate during a short-circuit (Fault Ride-Through - FRT), during the voltage level duration defined below at the connection point for fault conditions, sources must be capable of maintaining their connection to the network and stable operation.

Synchronous Sources:

| t [s] | U [pu] |
| --- | --- |
| 0.25 | 0 |
| 0.25 | 0.7 |
| 1.5 | 0.85 |

Table 11: Requirements for operation during a short-circuit - type D synchronous sources

Figure 9: Requirements for operation during a short-circuit – type D synchronous sources

Asynchronous sources:

| t [s] | U [pu] |
| --- | --- |
| 0.25 | 0 |
| 3 | 0.85 |

Table 12 Short-circuit operation requirements — Non-synchronous type D sources

Figure 10: Requirements for operation during a short-circuit – type D asynchronous sources

In case of asymmetrical faults, the same curves as for symmetrical faults shall apply.

### Voltage ranges – requirement for type D

Pursuant to Article 16.2(a) and (b) of Commission Regulation (EU) 2016/631 - without affecting the section entitled 'Operational capability during a short-circuit - requirement for type B and C sources' and the above section entitled 'Operational capability during a short-circuit - requirement for type D', the source must be capable of remaining connected to the network and operating within the following system voltage ranges at the connection point:

For the 110 kV voltage level:

- voltage range: 1.118 – 1.15 p.u.;

- running time: 60 min.

### Requirements for stabilisation feedback after a fault – requirement for type D synchronous units

Pursuant to Article 19.2 (b) of Commission Regulation (EU) 2016/631 - type D synchronous units with installed power of 50 MVA or more must be equipped with a system stabiliser to damp active power oscillations.

### Island operation – requirement for type C and D sources

Pursuant to Article 15.5 (b) of Commission Regulation (EU) 2016/631 - requirements are stipulated at points (f, U, LFSM-O, LFSM-U, FSM). Type C and D facilities (units) for the generation of electricity connected to the DS must be capable of participating in island operation. During such island operation, in its initial state the generating facility is galvanically isolated from the DS at the main disconnection point (MDP), which is switched off, and any changes in the operating state of the generating facility are coordinated with the DSO's control centre (DSO CC). If a request is issued for parallel operation with part of the DS, such operation is possible only following prior coordination with the DSO CC – for example during a black start, emergency situations in the system pursuant to § 3 of Act No 42/1994 on civil defence, or upon declaration of a state of emergency pursuant to § 20 of Act No 251/2012, the Energy Act. For parallel operation with part of the DS, a switching phase element must be installed in the power generation plant between the generator switch and the MIP.

### Loss of angular stability – requirement for types C and D

Pursuant to Article 15.6(a) of Commission Regulation (EU) 2016/631 – with regard to loss of angular stability or loss of control, the source must be capable of automatically disconnecting from the system in order to contribute to system safety or in order to prevent damage to the power-generating unit. Two pole slip events in a synchronous machine are used to detect loss of angular stability.

### Quick re-synchronisation/transfer to own consumption – requirement for types C and D

Pursuant to Article 15.5(c) of Commission Regulation (EU) 2016/631 - with regards to the ability to quickly restore synchronisation:

- if the source is disconnected from the network, it must be capable of quickly restoring synchronisation in accordance with the protection strategy approved by the appropriate system operator;

- a source with minimum synchronisation restoration time greater than 15 minutes after its disconnection from any outside source of power must be designed to transfer to own consumption from any operating point with its own P-Q figure;

- the source must be capable of continuing to operate once it has transferred to own consumption, regardless of any auxiliary connection to the external network (distribution system). The minimum internal consumption operation time shall be 2 hours.

### Settings of synchronisation devices – type D requirement

Pursuant to Article 16.4 of Commission Regulation (EU) 2016/631 - the owner of the generating facility may only perform source synchronisation following approval by the appropriate system operator. It must be possible to configure synchronisation device settings within the scope of the following parameters:

- voltage deviation ΔU of 30 % for voltage within permitted limits;

- frequency deviation of ±250 mHz over a frequency range of 47.5 – 51.5 Hz;

- phase angle range of ±10°;

- the phase sequence must be identical.

### Black start – requirement for types C and D

Pursuant to Article 15.5(a) of Commission Regulation (EU) 2016/631 - a black start must commence within 15 minutes of complete shutdown without any external sources of electricity. This condition applies to power-generating units with technology permitting black start.

### Period to reach the adjusted active power output set-point – requirement for types C and D

Pursuant to Article 15.2(a) and (b) of Commission Regulation (EU) 2016/631 – the regulating system of a source must be capable of adjusting the entered active power value in accordance with instructions from the DSO or TSO. The amount of time to achieve the desired active power value is as follows:

| The time to achieve a steady state within the tolerance band of the required active power reduction |  | The time to achieve a steady state within the tolerance band of the required active power increase |  |
| --- | --- | --- | --- |
| Synchronous sources | Asynchronous sources | Synchronous sources | Asynchronous sources |
| ≤ 30 s | ≤ 20 s | ≤ 6 min | ≤ 30 s |

Table 13: Required times for adjusting active power values for type C and D sources

The permissible deviation of actual active power from the required value is 2-10 % PN, but not more than 5 MW.

### Activation of active power output increase during under-frequency (LFSM-U) – requirement for types C and D

Pursuant to Article 15.2(c) of Commission Regulation (EU) 2016/631 - with regards to limited frequency sensitive mode, in order to minimise the impact on adjacent areas, the following requirements for activation of active power increase during underfrequency are applied:

- the frequency threshold for activation of change in active power output – 49.8 Hz;

- droop 5 %;

- the first reaction of the facility to a frequency change must occur within 2 seconds maximum. The owner of the facility must technically justify later activation of active power to the TSO.

### Active power response to a change in frequency FSM – requirement for types C and D

Parameters for activation of active power response pursuant to Article 15.2(d) of Commission Regulation (EU) 2016/631:

| Parameter | Value |
| --- | --- |
| Active power change | ±2 % PMAX |
| Droop | 2 – 12 % |
| Dead-band | ± 10 mHz |

Table 14: Required active power response upon frequency change (FSM)

The total reserve active power must be activated during a frequency deviation of ±200 mHz. The source must be capable of providing full frequency response (active power reserve) for at least 15 minutes. The full frequency response activation time must not exceed 30 s, including the initial delay, which must not be longer than 2 s.

### Frequency restoration control – requirement for types C and D

Pursuant to Article 15.2(e) of Commission Regulation (EU) 2016/631 – as regards frequency restoration control, the source must provide the following functions to restore frequency to its rated value:

- active power change range 40 % – 60 % PN;

- active power change rate 4 % PN/min.

### Active power change rate – requirement for types C and D

Pursuant to Article 15.6(e) of Commission Regulation (EU) 2016/631 - the minimum and maximum active power change limits at the source output (linear change limits) both upward and downward are as follows:

- minimum active power change at output 1 – 100 % PN/30 s

- maximum active power change at output 1 – 100 % PN/30 s

### Prioritisation of the active or reactive power contribution – requirement for type C and D asynchronous units

Pursuant to Article 21.3(e) of Commission Regulation (EU) 2016/631 - in the event of faults where operability during short circuit is required, asynchronous units of type C and D sources must preferentially provide active power within 150 ms of fault incidence.

### Power oscillation damping – requirement for type C and D asynchronous units

Pursuant to Article 21.3(f) of Commission Regulation (EU) 2016/631 - type C and D asynchronous units with installed power of 5 MVA or more must be capable of contributing to the damping of active power oscillations.

### Instrumentation/damping of power oscillations – requirement for type C and D sources

Pursuant to Article 15.6(b) of Commission Regulation (EU) 2016/631:

Fault recording equipment:

Type C and D sources must be equipped with monitoring devices logging selected quantities (P, Q, U, f) over an interval of 5 to 15 minutes, sampling at least every 0.1 s (optimally every 0.05 s) when rated voltage limits are exceeded by ± 5 % or 50 Hz frequency by ± 200 mHz. This interval is recorded on electronic media and is archived, available upon request to the system operator. Measurement precision is 0.1 % for voltage and power and 0.01 % for frequency.

Equipment for monitoring the dynamic behaviour of the system:

Type C and D sources must be equipped with instrumentation for the monitoring of frequency fluctuations within the range of 0.2 – 3.5 Hz, logging selected quantities (P, Q, U, f) over an interval of 0 to 20 minutes, sampling at least every 0.1 s (optimally every 0.05 s) when fluctuation amplitude of 2 % of the supplied active power is exceeded, or during fluctuation damping x<5 %, x=(A1-A2)/A1, where A1 and A2 are two consecutive active power fluctuation amplitudes. In addition to P, Q and frequency, the instrumentation shall also record voltage and current for each phase. Logging shall be identical to that for fault recording.

### Simulation models – requirement for types C and D

Pursuant to Article 15.6(c) of Commission Regulation (EU) 2016/631 - if requested by the DSO or TSO, the source owner must provide models for verification of behaviour of sources during steady state, during transients and for simulation of electromagnetic transients. The information contains documentation for models of individual parts of the facility (block diagrams and their parameters):

- the alternator and its motive unit;

- RPM and power regulation;

- voltage regulation, including a system stabiliser and an excitation regulation system if applicable;

- source protection models pursuant to an agreement between the DSO and the source owner,

- models of converters and asynchronous modules.

Simulation models shall be provided in a format compliant with IEC standards (61970-302, 61400-27-1).

### Monitoring of active power response to frequency changes – requirement for types C and D

Instrumentation for monitoring active power response to frequency changes – requirement for types C and D

Pursuant to Article 15.2(g) of Commission Regulation (EU) 2016/631 – for purposes of monitoring the response of active power to frequency changes (FSM), the communication interface (for type C and D sources) must be equipped for secure real-time transmission from the source to the control centre.

| Monitoring active power response to frequency changes on source terminals |  |
| --- | --- |
| Signalling: | Quantity |
| Monitoring status | off/on |
| Set value: |  |
| Scheduled P | [MW] |
| Measurement |  |
| Actual P | [MW] |
| Droop | [%] |
| Dead-band | [mHz] |

Table 15 Required signal range for monitoring response P to frequency changes on terminals of type C and D sources

### Requirements for reactive power for synchronous units on types C and D

Pursuant to Article 18.2 of Commission Regulation (EU) 2016/631 - synchronous units of type C and D sources must be capable of delivering additional reactive power. This additional reactive power must compensate the consumption of reactive power on high voltage lines or cables between the high voltage terminals of the block transformer of a power-generating unit or the terminals of its alternator, if there is no block transformer, and the connection point.

If maximum power P is being delivered, the generating unit must be capable of operating within the limits stipulated in the figure below, unless specified otherwise by the appropriate system operator.

Figure 11: Reactive power requirement diagram for synchronous units of types C and D

| Pevná vonkajšia obálka | Fixed outer envelope |
| --- | --- |
| Vnútomá obálka | Inner envelope |

If the delivered power is lower than maximum, the source must be capable of operating within the scope of the generator's PQ operating diagram.

### Reactive power requirements for asynchronous units of types C and D

Pursuant to Article 21.3(b) and (c) of Commission Regulation (EU) 2016/631 - type C and D asynchronous units must be capable of supplying additional reactive power. This additional reactive power must compensate the consumption of reactive power on high voltage lines or cables between the high voltage terminals of the block transformer of a power-generating unit or the terminals of its alternator, if there is no block transformer, and the connection point.

If maximum P is being delivered, the generating unit must be capable of operating within the limits stipulated in the diagram below, unless specified otherwise by the DSO.

Figure 12: Reactive power requirement diagram for asynchronous units of types C and D at maximum power

| Pevná vonkajšia obálka | Fixed outer envelope |
| --- | --- |
| Vnútomá obálka | Inner envelope |

If the supplied power is lower than the maximum capacity, the source shall be capable of operating within the range in the diagram below.

Figure 13: Reactive power requirement diagram for asynchronous units of types C and D at less than maximum power

| Pevná vonkajšia obálka | Fixed outer envelope |
| --- | --- |
| Vnútomá obálka | Inner envelope |

Installations with reactive power regulation, requirements for reactive power of sources

Voltage quality requirements, especially compliance with permissible voltage range, are a critical factor when connecting sources to the DS. In their operation, the sources increase the voltage in DS and must therefore contribute to the stabilisation of the voltage through reactive power control within a defined range. They are operated in the range between capacity (reactive energy consumption) to neutral power factor.

The DSO specifies the reactive power regulation method after consulting with the source operator, which always depends on the specific location in the DS. For regulation of reactive power at a connection point, the DSO specifies a fixed value or a required value configurable using remote control equipment.

The required value may be:

- maintaining a fixed power factor value cos j (sufficient for sources up to PN < 1 MW);

- maintaining the power factor value cos φ = f (P);

- the assigned reactive power value (consumption/supply) within the scope of the reactor’s P/Q diagram;

- maintaining standardised voltage at the connection point, at the generator output, past the block transformer, or at the pilot node within the scope of restrictions on the P/Q diagram.

Failure to comply with reactive power regulation specifications, failure to adhere to the prescribed source power factor cos φ is subject to proceedings pursuant to applicable legislation, and this fact is seen as failure to comply with the DSO's technical specifications.

- Sources connected to the LV system up to and including 4.6 kVA/phase

A source’s power factor cos φ under normal, stabilised operating conditions at the permissible tolerance range for rated voltage must be between 0.95 and 1 capacitive, assuming that the active output component is over 20 % of its rated output. These sources must not supply reactive power to the grid.

Note: A capacitive power factor represents reactive power consumed by the source. An inductive power factor represents reactive power supplied by the source.

Power factor compensation is usually not required for photovoltaic plants with an output of up to 4.6 kVA per phase if they maintain a capacitive generation characteristic between 0.98 – 1, i.e. if this source does not supply reactive power to the LV system.

- Other sources connected to the LV network

A source’s power factor cos φ under normal, stabilised operating conditions at the permissible tolerance range for rated voltage must be between 0.95 and 1 capacitive, assuming that the active output component is greater than 3 % of its rated output.

- Sources connected to the HV network

Source reactive power consumption must be configurable for every source connected to the HV network. A generator must be capable of delivering the rated active power within the basic regulation range of the capacitive power factor cos φ = 0.95 to 1 (generator operation in underexcited state) at the permitted voltage at the terminals of the generator ± 5 % Un and at a frequency between 47.5 and 51.5 Hz. At lower active power values, the permitted reactive power values are determined according to the so-called ‘Operational Generator Diagrams’ (P/Q diagrams), which must be part of the block's design documentation. If the technologies of the power plant’s own consumption and provision of power for its own consumption make it impossible to use the above permitted range (the voltage for own consumption would be outside the permitted range), it is possible to increase the regulation range of the generator, for example by using a tap-changing transformer for power for own consumption with regulation under load. The specified basic required regulation range of reactive power may be modified, thus narrowed or broadened. The reason for this modification may, for example, be different (higher/lower) consumption of regulating reactive power in the given part of the DS or special technological reasons (asynchronous generators). Such modifications presuppose a special agreement between the source operator and the DSO.

When choosing compensation equipment, it is necessary to take into account how the source operates and its resultant effects on the DS. For heavily fluctuating output (such as certain types of wind power plants), reactive power compensation must be automatic and must be regulated sufficiently rapidly.

The mode of operation of any compensation capacitors and silencers in relation to the operation of the generator shall be determined by the DSO.

The operation of sources may require action to limit harmonic voltages. The DSO must approve the output, connection, and regulation method of compensation equipment, and potentially compensation for harmonics by means of suitable inductions (compensation elements).

- Configurable fixed power factor cos φ

The DSO will agree with the source operator on a power factor cos φ, so that the source can supply the required active power. Recommended settings:

- for sources connected to the LV network within the range of 4.6 kVA/phase to 30 kVA: cos φ = 1;

- at higher power levels a different value corresponding to the source's point of connection to the distribution system may be specified.

Devices with non-regulable/non-configurable reactive power

If reactive power cannot be regulated or adjusted (only permissible for sources in the LV network), the cos φ power factor must be within the following limits unless the DSO determines otherwise with respect to a specific connection point to the DS:

- Generation: 2nd Quadrant: 0.98-1.0 takes reactive power from the network (2nd quadrant — capacitive source).

- Consumption: 1st Quadrant: 0.95 to 1.0 (the equipment is an appliance, consumes active power from the network and also consumes reactive power (1st quadrant — inductive appliance).

- Reactive power compensation

In order to avoid high active power losses, it is necessary to maintain a capacitive power factor cos φ of 0.95 ÷ 1. In a DS with a high proportion of cables and with capacitors of existing compensation equipment, the total power factor can be in the capacitive area. Compensation devices must not result in capacitive power being supplied to the distribution system. For that reason, the DSO may waive the requirement for compensation devices in individual cases, such as with small asynchronous generators. Depending on conditions in the DS and the user’s electrical facilities, the DSO may require individual, group, or central compensation.

When using compensation capacitors, the risk of resonance must be minimised. At a frequency higher than 50 Hz, parallel resonance occurs between the stray reactance of the supply transformer and the totals of all network capacities, and increased network impedance may result, primarily in periods when the load is light. Connection of compensation capacitors shifts this resonance frequency downward. This can lead to an increase in harmonic tensions in some HV systems. To prevent this situation, compensators may be protected with current-limiting induction (this is not always sufficient, because it increases the voltage in the capacitors).

Upon disconnection, a charge may remain in the capacitors which, without bleeder resistors, may cause a higher contact voltage than is permissible pursuant to applicable standards. A capacitor may also be damaged if it is switched back on while still charged. For that reason, bleeder resistors are necessary, primarily at higher power levels, or suitably connected instrument voltage transformers may be used for discharge.

- The need for reactive power from asynchronous generators

The reactive power needed from an asynchronous generator is approximately 60 % of the supplied apparent power. If this reactive power is not to be supplied by the DS, it is necessary to connect corresponding capacitors parallel to the generator for compensation. Since an asynchronous generator may only be connected to the network in a zero-voltage state, the applicable capacitors may not be connected before the generator is connected. In order to do this, the switch-on command may, for example, be derived from an auxiliary contact of the coupling disconnect switch. When shutting down the generator, it is necessary to disconnect the capacitors to prevent self-excitation of the generator and to protect from back voltage.

- The need for reactive power from synchronous generators

In the case of synchronous generators, cos φ may be set via excitation. Depending on the type and size of the drive unit, either constant excitation will suffice, or a regulator for voltage or cos φ is needed.

Unambiguous assignation of ranges for the power factor cos j is possible using the following table.

| Example | Source orientation | Consumption orientation |
| --- | --- | --- |
| Synchronous generator (over-excited) | P > 0 and Q > 0 0° < φ < 90° | P < 0 and Q < 0 180° < φ < 270° |
| Asynchronous generator | P > 0 and Q < 0 270° < φ < 360° | P < 0 and Q > 0 90° < φ < 180° |
| Synchronous motor (over-excited) | P < 0 and Q > 0 90° < φ < 180° | P > 0 and Q < 0 270° < φ < 360° |
| Asynchronous motor | P < 0 and Q < 0 180° < φ < 270° | P > 0 and Q > 0 0° < φ < 90° |

Table 16 : Assignation of power factor ranges

- The need for reactive power for inverters

Sources with inverters controlled by network frequency have an idle output consumption approximately corresponding to that of an asynchronous generator. For that reason, the same conditions as for asynchronous generators apply to the compensation of these inverters.

Sources with inverters with self-synchronisation consume insignificant reactive power, so generally do not require reactive power compensation.

# ELECTRICITY METERS, METERING AND CONTROL EQUIPMENT

For purposes of this annex, the term metering is defined as billing metering installed in an electrical meter switchboard or in a different manner approved by the DSO.

The type and number of metering devices and elements of metering sets, their composition, and technical parameters are defined in the document ‘Electricity Metering Specifications’ listed on the DSO’s website, which also analogously apply to sources, unless specified otherwise in these DSO TS. The placement of metering devices must be agreed upon with the DSO no later than the design approval phase for a construction permit.

In general, any new source will be measured by an intelligent meter with continuous measurement and remote data collection. The DSO supplies and installs metering devices. Current and voltage instrument transformers are part of source equipment. Instrument transformers must be specified measuring instruments of an approved type; they must have the required technical parameters, and should have official verification valid within the Slovak Republic.

The measurement type and method in the area of electricity supply at the VHV and HV levels is specified based on the value of the maximum reserved capacity (MRC), which is a contractual value. In the area of electricity supply at the LV level, it is specified based on the current value of the main circuit breaker agreed upon during the process of approval of specifications for the connection of the source to the distribution system, or contractual reserve capacity values.

The source operator, pursuant to applicable legislation, has the right to install their own metering on the generator terminals.

The DSO decides on the location and connection method for metering devices and their accessories. In general, this is also affected by the source operator’s request for the operating method of the source, split as follows:

- entire production to the DS;

- excess production to the DS.

All costs related to setting up a metering point (aside from electricity meter costs) and its operation are borne by the producer or source operator. The manner, conditions, and due dates for submitting actual measured values for a producer with the right to support pursuant to special legislation are regulated by the DSO in its operating regulations.

Connection of a source to third-party electrical equipment must not result in transit metering of electricity. Transit metering is defined as billing metering devices being arranged in a series (metering on generator terminals for purposes of supporting the production of electricity through a surcharge is not considered billing metering). Connecting a source to third-party electrical equipment that is not the property of the DSO is not cause for changes to the location of existing electricity metering unless the DSO decides otherwise.

  - Situation of metering devices

Metering devices for sources are designed in accordance with the document ‘Electricity Metering Specifications’ available on the DSO’s website.

Locations of metering devices depending on power level, operating method, and connected voltage level are shown in 'Figure 1' to 'Figure 6' of this annex.

If consumption equipment already exists at the same connection point, the metering devices must be situated so that the amount of consumed and supplied electricity are determined in an unambiguous manner.

In the case of sources connected to the HV network, electricity metering (if it is installed in a substation that does not belong to the DSO) must be situated in a publicly accessible location. In the case of fenced-in properties, this requirement can be fulfilled by placing a substation with outdoor access to metering devices at the edge of the property (for example as part of the fence). If such a technical solution is demonstrably financially costly, a written agreement between the DSO and the source operator is required regarding conditions for access by DSO employees to metering devices.

  - Requirements for cooperation with control and information systems

Sources connected to the DS with a total installed output of 100 kW and higher (type B, C and D sources connected to the DS) must be remote controlled, signalled, and measured from the applicable DSO central control centre in accordance with the DSO TS and the requirements of standardisation of control and information systems of central control facilities and operators’ energy facilities. For sources with total installed output up to 100 kW (type A sources), the DSO will perform an individual assessment of the need to connect the source to the DSO’s control system and to comply with the requirement to cooperate with CIS.

A switching element controlled from the DSO CC must always be a MIP. Requirements for connecting source control systems to the central control are implemented according to the principles of the DSO.

The minimum scope of transmitted data for central control is defined in Chapter 2.3 of the main part of this document:

The data connection can be implemented in two basic ways – as a 'fixed connection' or as 'a VPN connection'.

- Fixed connection.

Such a connection is preferred in the case of sources with an installed power of over 1 MW, or those that are connected to the DS with a separate line connected to the VHV/HV network. A fixed connection via the IEC60870-5-101 protocol over two independent fixed lines to the DSO’s central control (CC) and central backup control (CBC) facilities. These fixed connections are implemented as two independent optical routes combined with the DSO’s TWAN infrastructure, or as routes provided as part of third-party services.

Implementation and operation principle:

The source operator will build two independent communication interfaces on the source technology using the IEC60870-5-101 protocol with parameters defined by the DSO.

The scope and form of data provided on these interfaces, which are identical from a data perspective, are specified in advance by the DSO pursuant to applicable DSO Technical Specifications for each specific case, primarily based on the type, size, and connection point of the source and its relevant subsystems as a comprehensive whole, and based on DSO CC requirements for the specific source.

The source operator will build two independent serial communication lines from the building housing the source to the building housing the DSO CC and the building housing the DSO CBC. If the source is directly connected to the DSO’s DS with a separate line to the electrical system (ES), an optical cable (interconnection) between the source building and the relevant DSO ES needs to be addressed within the scope of the power connection. In this case, another route (between the relevant ES and CC or CBC) will be addressed in existing DSO communications infrastructure. In this case, it is possible to utilise free capacity in this optical interconnection for eventual addition of a network voltage quality analyser or other devices requiring a communications interconnection between the source building and DSO facilities.

DSO CC and CBC hardware will be augmented with one serial communications port in each control room with relevant parameters.

DSO CC software will be supplemented with data defined in the requirements for the scope and form for a specific source at all its levels.

Communication connections are activated up to the application layer of the IEC60870-5-101 protocol, and functional tests involving the transmission of specific data points defined in the data model to individual DSO CC facilities are performed.

Data communication up to the DSO CC serial interface is fully under the control of and the responsibility of the source operator (aside from the case when part of the DSO’s communication infrastructure is used for communication, when this part is under the control of and the responsibility of the DSO).

- Connection via a VPN

This connection is preferred for sources with installed power up to 1 MW. If an individual assessment shows that this method makes more economic and technical sense, this connection can also be used for higher-power sources. Connection via a VPN uses a secure communication channel over the internet.

Implementation and operation principle:

The source operator will build one communication interface on the source technology using the IEC60870-5-104 protocol with parameters defined by the DSO.

If the type of hardware (including its software version) that will be used to create this communications interface is not connected to the DSO CC, the DSO reserves the right to test this communication with the given hardware in laboratory conditions on the DSO’s premises – an acceptance test.

The scope and form of data provided on this interfaces (data model), which are identical from a data perspective, are specified in advance by the DSO pursuant to applicable DSO Technical Specifications for each specific case, primarily based on the type, size, and connection point of the source and its relevant subsystems as a comprehensive whole, and based on DSO CC requirements for the specific source.

The source operator will arrange and subsequently operate a VPN connected to the internet terminated on the DSO's dedicated VPN concentrator pursuant to required characteristics and specific settings defined by the DSO individually for each case.

This connection will be used solely for the communication between the source technology's interface and the DSO CC using the IEC60870-5-104 protocol.

DSO CC software will be supplemented with data defined in the requirements for the scope and form for a specific source at all its levels. The communication connection will then be activated, and functional tests involving the transmission of specific data points defined in the data model to individual DSO CC facilities will be performed – physically from the source technology to the DSO CC.

Operation of the source technology communication interface as well as data communication up to the DSO's VPN concentrator is fully under the control of and the responsibility of the source operator. The inability to provide data for central control or any errors in this data are considered failure to comply with technical specifications for connection to the DS and must be eliminated immediately. Otherwise, operation of such a source will not be permitted or it will be disconnected from the DS.

# CONNECTION SPECIFICATIONS

This chapter specifies electricity indicators that must be maintained within the given limits, thus affecting the DS connection location and method from the perspective of evaluating back effects on the DS.

In order to prevent back voltage from being introduced into the DSO’s network, it is necessary to take technical measures to ensure that the connection of a source to the DS is only possible when all phases of the network are under voltage. A switch that connects the customer’s entire facility with the network can be used for connection, but so can a switch that connects the generator or multiple parallel generators with the customer’s remaining equipment. Activation of a coupling switch must be blocked until each phase has the required minimum voltage for undervoltage protection activation. A suitable time delay between voltage restoration in the DS and connection of the source is recommended.

When connecting multiple generators at one common connection point, the time intervals must be coordinated with the DSO.

After a shutdown by protective devices, the source may not be started up until the fault that led to the shutdown has been eliminated. After work on source equipment and the feeder to the DS, it is above all necessary to check for correct phase sequence.

After the source has been shut down by DSO employees, its activation must be agreed upon with the relevant DSO facility. The relevant DSO CC (pursuant to the LOR) must be notified of activation in advance, unless otherwise agreed upon.

The delay before reconnecting the generator and time intervals at which multiple generators are connected must be long enough to ensure that all regulation and transient events have been completed. During motor start-up, the current in asynchronous machines is several times the rated current. Given high current and voltage dips in the network (the degree of flicker perception Plt), motorised start-up of generators is generally not recommended.

In order to establish conditions for synchronisation, synchronisation equipment must have a measuring part containing a dual frequency and voltage meter and a differential voltage meter. Automatic synchronisation is recommended. If a proprietary source is not fitted with a sufficiently fine regulation and rough synchronisation occurs, it will be necessary to fit it with a choke coil to limit current surges. With inverter equipment, it is necessary to use a control thyristor to ensure that the inverter is not under power on the DS side before connection.

  - Voltage increase

In the worst-case scenario, an increase in voltage caused by the operation of connected sources may not exceed 2 %, at the connection point for sources with a connection to HV and VHV networks, in comparison with the voltage value when the sources are not connected:

Δuhv, vhv ≤ 2 %

for a source with a connection point in the LV network, the voltage increase must not exceed 3 %, i.e.:

Δulv ≤ 3 %

If there is only one connection point in the LV or HV network, it is possible to apply the above conditions and stipulate maximum connectible source power SAmax as follows:

SAmax ≤ 2 %*SkV / (cos(ψkV-φ)) ≤ SkV/(50*(cos(ψkV-φ))) for VHV and HV connections

SAmax ≤ 3 %*SkV / (cos(ψkV-φ)) ≤ SkV / (33*(cos(ψkV-φ))) for LV connections

using short-circuit power at the connection point SkV = 0.9*S’ kVmaxthe short-circuit impedance angle of the system at the connection point, kV and the phase angle j between the current and the voltage of the source at the maximum apparent power SAmax .

To determine SAmax in the case of wind power plants, it is necessary to rely on the maximum apparent capacity of the individual installation SEmax:

SEmax = SEmax 10 min = SnG * P1 min = PnG / λ * P10 min

where it is necessary to take the value p10 min (maximum mean output at 10-minute intervals) from the assembly test results. For a source that has a special device for limiting power output, limited power values must be used.

In the case of the only connection point in the network, the voltage increase criterion of 2 %, or 3 %, will always be complied with when the short-circuit power ratio kk1 for sources with a connection point in the HV network is as follows:

similarly, for sources with a connection point in the LV network:

In the case of sources that supply reactive (inductive) power to the network (for example, excited synchronous generators, impulse converters), the following applies: P > 0 and Q > 0, 0° ≤ φE ≤ 90°. For sources that source reactive (inductive) power (e.g. asynchronous generators, induced synchronous generators, network-controlled inverters), the following shall apply: P > 0 and Q < 0, 270° ≤ φE ≤360° (-90° ≤ φE ≤0°). If the value of the term cos (ykV – j) in the formula is less than 0, then, taking into account the degree of uncertainty of this calculation, it is estimated at 0.1.

In many cases a given practical maximum connectible power of SAmax is given, for which it is then necessary to specify a voltage increase at the connection point. For this purpose, the following relationship is used:

Δu AV = SAmax * cos(ψkV-φ)/ SkV

The change in system voltage when switching the source can be estimated based on the ratio of the short-circuit power value in the network PDS Skv and the nominal apparent power of the source SnE according to the relationship:

Δu max = ki max * SnE / SkV

where the coefficient kimax , referred to as the ‘maximum switch-on surge’, indicates the ratio of the greatest current occurring during the switching march (e.g. Ia ) and the rated current of the generator or device:

ki max = Ia / InG

Values obtained using this ‘maximum switch-on surge’ provide certainty that results will be within the range of correct values.

For the switch-on surge coefficient, the following guideline values apply:

kimax = 1	synchronous generators with fine synchronisation, inverters

Kimax =4, asynchronous generators connected at 95-105 % of synchronous speed, unless more precise data on the possibilities and method of limiting current are available, taking into account the short-term transient phenomenon, the following condition for very short voltage drops must be respected

Kimax = I a /I nG asynchronous generators motor-assisted from the network

Kimax = 8 if I a is unknown

Asynchronous machines connected with approximately synchronous rotation may cause very short voltage dips due to internal transient effects. Such a dip may reach two times the otherwise permissible value, which is 4 % for HV and 6 % for LV, as long as it does not last longer than two periods and the following deviation in voltage from the value before the voltage dip does not exceed the otherwise permissible limit.

A special ‘network-dependent switching coefficient’ applies to wind electrical plants, which is used to evaluate their switching and which simultaneously takes into account the aforementioned very short transient effects. The coefficient takes into account not only the magnitude but also the variation in the current during the transient effect, and is given as a function of the network impedance angle y. The manufacturer must certify this coefficient in the test certificate for each piece of equipment. This coefficient can be used to calculate a fictitious ‘substitute voltage change’:

Δu ers = kiψ * SNe / SkV

This change also (as Dumax) must exceed 2 % for sources with an HV connection point, and 3 % for sources with an LV connection point.

In order to minimise back effects on the DS, it is necessary to ensure that multiple generators do not switch on simultaneously at one connection point. A solution is to stagger individual switching on over time; this depends on elicited voltage changes - at maximum permissible generator power it is at least 1.5 minutes, while with apparent generator output at half the permissible value, 12 seconds is sufficient. In the case of very infrequent switching, for example once per day, the DSO may allow greater voltage changes during switching if network conditions allow.

  - Connection of synchronous generators

When connecting synchronous generators, it is necessary for them to be equipped with synchronisation equipment that allows the following synchronisation conditions to be met:

- voltage difference ΔU < ± 10 % Un;

- frequency difference Δf < ± 0.5 Hz;

- phase difference < ± 10°.

Depending on the ration of system impedance to generator output, lower limits may be stipulated for switching if necessary in order to prevent inadmissible back effects on the network.

  - Connection of asynchronous generators

Asynchronous generators started by an actuator must be connected without voltage at rotation within the boundaries of 95 % – 105 % of synchronous rotation. For asynchronous generators that are not connected under zero voltage, it is necessary to comply with the same conditions as with synchronous generators.

  - Connection of sources with inverters, with frequency changers

Inverters may only be connected if their AC side is not under power. For sources with inverters that are capable of island operation and are connected under power, it is necessary to comply with the conditions that apply to synchronous generators.

  - Connection of sources to the 110 kV network

A special agreement regarding the design of system protection, blocks, and regulation must be reached with a source operator connected to the 110 kV network. In the network analysis it is also necessary to evaluate the stability of the resource. In the case of connection of a source to a 110 kV network, requirements of the TSO’s technical specifications must also be met.

  - Connection checks for cumulative power

In the case of cumulative installed source power, for VHV/HV transformation, free capacity can be defined according to the following procedure while complying with other technical specifications of the DSO:

SMAX = (SINS * kTR + SBIL) * kE2

where:

SINS — installed capacity of the smallest transformer in the substation;

kTR – a reduction coefficient that takes into account optimum transformer loading (unless use of another value is justified, 0.9 is used),

SBIL – the minimum load in the area powered from the substation under consideration; it is necessary to subtract the installed power of all existing sources connected in the powered area;

kE – a reduction coefficient taking into account small, dispersed production on the LV side into a defined installed capacity.

# BACK EFFECTS ON THE DISTRIBUTION SYSTEM

To avoid interference with other customers’ equipment and DSO equipment, it is necessary to limit the back effects of local sources on the DS. Assessment is based on principles for assessing back effects and their permissible limits specified in Chapter 2.2 of these technical specifications.

# SOURCE COMMISSIONING

A source may only be connected to the DS if the DSO’s technical specifications are met. A ‘technical inspection’ and then ‘functional tests’ of the source must be performed in order to check that technical specifications have been met.

In the case of a source in the energy business, or in the case of an LSE above 11 kW, a technical inspection and functional test are always performed. For sources that are not in the energy business (SSE and LSE up to 11 kW, or 16 A per phase), a technical inspection and functional test are performed only in cases corresponding to provisions of Act No 309/2009, on support for renewable sources of energy and highly efficient co-generation.

  - Local operation regulations, technical inspection

No later than 30 calendar days prior to the planned technical inspection, a source operator in the energy business and an LSE over 11 kW must submit local the electrical engineering portion of operating regulations for the source to the DSO for approval (digitally to the address specified in the DSO's response).

The DSO will ensure that the local operating regulations (LOR) are commented on within 15 workdays of their delivery; repeat rounds of comments are subject to the same deadline. Local operating regulations will, among other things, define the obligations and procedures of the source operator and DSO in operating power facilities and during emergency operating conditions.

A source operator in the energy business and LSE above 11 kW (or 16 A per phase), have approved LOR by the date of the technical inspection.

When drawing up local operating regulations (LOR) for a source, the following is taken into account:

- the source type and its operating options;

- DS operating requirements;

- legitimate interests of the source operator;

- compliance of source operation with Slovak energy policy.

The LOR must contain at least the following:

- Introduction

- General description of the source

- Source operation, a description of all possible operating states

- Technical design, single-pole connection schematics with element descriptions

- How the source’s electrical power is fed to the distribution system

- Technical data for the source

- Transmission of source operation information

- Manipulating the source

- Source outage procedure

- Distribution system outage procedure

- Planned source shutdowns

- Grounding

- Safety instructions

- First aid in case of electrical shock

- Obligations of the source operator

- Obligations of operating personnel in case of an electrical equipment fire

- Authorised individuals and phone numbers (source operator, etc.).

- A list of the most important phone numbers for central control

- Signatures

- Annexes

A sample of LOR for sources that are in the energy business and LSE over 11 kW that connect at the LV and HV level is provided on the company's website.

The applicant for connection shall notify a DSO employee of the proposed date for a technical inspection (via email or in writing). After coming to an agreement with the participants in the technical inspection, the proposed date is approved, or the DSO employee proposes a new one.

The applicant for connection must deliver to the DSO the following documents no later than when proposing the technical inspection date:

- A completed ‘Table of Generator Parameters_Compulsory Annex to the TI’ (for rotary generator)

- As-built design documentation in paper and digital form (CD,DVD).

- A post-installation survey in digital form (.dgn, .dxf, or .dwg file format), if requested by the DSO.

- Instrument current transformer and instrument voltage transformer verification certificates valid in the Slovak Republic.

- A technical inspection and technical test report for electrical equipment.

- An official test certificate for specified equipment (SE) from a technical inspection facility or an expert opinion on an official test of SE from a technical inspection employee. In the case of a substation, it is possible to submit a declaration regarding the condition of electrical equipment confirmed by a qualified professional pursuant to the applicable decree. After the substation is switched on, the first technical inspection and test on the given equipment must be performed, no later than by the date of functional testing.

- An expert opinion regarding building design documentation issued by an authorised corporate subject, pursuant to a licence issued by the National Labour Inspectorate.

- A building permit for the relevant structure or final building approval decision or an interim use permit, if the structure is subject to building permit proceedings.

- Photocopies of test reports and type sheets by an accredited service (Slovak translation) with technical data of the equipment (generator, transformer, inverter, compensation device, etc.). these documents shall also be submitted on CD or DVD.

- Source operation method, test reports, and a type test report for static inverters, with a report on expected current harmonics and interharmonics, if requested by the DSO.

- An exact schedule of activities and measures carried out during the technical inspection, if requested by the DSO.

- Local operating regulations for the source – electrical equipment part (LOR) approved by the DSO (signed on the cover page by the author of the LOR, the source operator, and DSO employees).

During the technical inspection, the source is not connected to the DS, even for test purposes. During the technical inspection, confirmation and a check of compliance with technical specifications and conditions specified by the DSO is required.

A representative of the DSO shall issue a written report on the technical inspection within 3 workdays of the technical inspection. The technical inspection record will include a completed ‘Table of Generator Parameters_Compulsory Annex to the TI’ (for rotary generators). The DSO representative will also inform the source operator of the identity of the contact person for carrying out functional tests.

Billing metering can be installed only after a successful technical inspection (a positive technical inspection report is required).

In the case of biogas plants (BGP), a temporary source activation permit allows installed BGP technology to be configured to prepare the biogas utilisation process. An applicant for a temporary source activation permit must apply in writing to the DSO at least 5 workdays prior to turning it on. A temporary source activation permit can be exercised based on an agreement with the DSO and the conditions in point 8.1.

  - Functional tests

For an SSE that does not operate in the energy sector and LSE up to 11 kW (or 16 A per phase), the functional test of the source is replaced by the Operations Notification, the form of which is provided on the DSO website. The distribution system operator has the right to request a producer of electricity from a small source, in writing, to perform a functional test for reasons specified in Act No 309/2009, on support for renewable sources of energy and highly efficient co-generation, and on changes and amendments to some acts.

In the case of a source operator in the energy business and LSE above 11 kW (or 16 A per phase), commissioning is contingent on passing functional tests. A functional test date can be requested once the source has passed the technical inspection, or once shortcomings found during this inspection have been eliminated. No later than 30 calendar days before the planned execution of functional tests, the source operator must submit the following to the DSO for approval (in digital form to the address specified in the DSO’s response):

- a precise substantive plan and schedule (SPS) for functional tests, if required by the DSO;

- the date of functional testing of the data connection (if used), which must take place no later than the day of the functional tests of the source (a data connection functional test report is required).

By mutual agreement, a precise date will be set for functional tests so that network operations staff will have at least four workdays prior to the date of the tests to incorporate the test date into the work management plan.

During functional tests, the source operator must deliver:

- an ‘Electrical Protection Settings and Functional Tests Report’ according to DSO requirements;

- a report on the successful performance of data connection tests, if a data connection was requested from the DSO (approved by the responsible DSO employee).

DSO representatives manage, but do not perform, the functional tests. The source operator must arrange personnel who are authorised to work on electrical equipment to perform the functional tests.

An important part of checks prior to connection is the execution of functional protection tests. These are performed either in real conditions or via simulation using appropriate test instruments.

It is necessary to carry out protection activation tests and compliance with the prescribed disconnection times for the following operating conditions:

- a single-phase and three-phase system outage;

- source reconnection after loss of power from the DS;

- if applicable, also frequency deviations (simulation using test equipment).

Similarly, it is also necessary to perform these tests for sources with inverters. It is necessary to test the correct operation of measuring devices (active and reactive components). If the source is equipped with remote control, signalling and measurement, it is necessary to verify their function from the relevant interface.

If required by the DSO, it is necessary to check the functionality of compensation equipment, whether it is to be connected and be disconnected simultaneously with the generator, and in the case of regulation equipment, whether regulation corresponds to the power range. Confirmation of compliance with the conditions set out in Chapter 6 of this annex is required, in particular the measurement of back effects (if requested by the DSO). Commissioning, functional testing, etc. must be documented in the relevant test report.

Expected range of testing:

- A check of connection accuracy (for example, checked when converters are switched on under voltage with no load).

- A check of current, voltage, and rotating field magnitude (load current > 10 %).

- A check of the direction of load current (load current > 10 %).

- A check of the signs of P and Q measurements. (On protective terminals where the sign for P and Q cannot be set regardless of the protective function, ‘+’ is set for power supplied to the line and ‘-’ for power supplied to the busbars. For display in the schematic for the relevant field, ‘+’ will be displayed for power supplied to the busbars and ‘-’ for power supplied to the line).

- A check of coordination with protective equipment (PE) automation, disconnect switch, and fault signalling.

  - Verification of monitoring of the ‘PE-NO PE’ switch on the PC

  - Verification of use of the PE switch using the PC

  - Place the PE switch in the ‘1 pole PE’ position - test 1-pole faults

  - Place the PE switch in the ‘3 pole PE’ position - test 1, 2 and 3-pole faults

  - Place the PE switch in the ‘1+3 pole PE’ position - test all variants

  - Place the PE switch in the ‘NO PE’ position - test all variants

  - Measure the no-voltage pause on the power disconnect switch (1 and 3 pole PE)

  - Check of pole discrepancy.

Before performing functional tests and placing the source into test operation, the source operator must confirm that the source was built according to regulations, standards and principles, such as:

- currently applicable laws and implementing legislation;

- applicable EN, STN, and PNE standards and the DSO’s technical specifications;

- employee protection and occupational safety regulations;

- the DSO’s regulations and guidelines.

After functional tests are complete, the source is usually disconnected from the DS. The source may remain in permanent operation only if all technical and commercial conditions for connection of the source are met, within the meaning of Chapter 8.3.

  - Approval of permanent source operation

The DSO will decide whether, during or upon completion of functional testing of the source, it will perform any other necessary tests and measurements. The DSO will add the results of these checks to the functional test report for the source.

A report on successful functional tests of the source is required for signature of a contract for supply of electricity from the source. Only once it has been signed can the source be connected to the DS pursuant to the approved LOR.

If so requested by the DSO, all new and reconstructed equipment connected to the DSO’s DS is commissioned according to an operating test programme drawn up by the investor, in cooperation with the contractor and operator. This programme is approved by the DSO.

A request for placing a source into permanent operation and approval thereof must be submitted according to the DSO’s operational preparation phases. Specific deadlines and methods for submitting requests for DSO operational preparations are defined in the DSO’s operating instructions published on the company’s website.

Commissioned equipment is considered to have been accepted under central control only after:

- compliance with conditions for connection to the TS specified in the Codex of the TS SR;

- completion of all prescribed and agreed-upon operating tests;

- approval of LOR for the source by the DSO;

- delivery of all documents necessary for central control of the facility (information systems);

- functional verification of telecommunications connections and information and control technologies;

- the operator’s declaration that the equipment is capable of operation.

An order from the source’s operations service for manipulation must be performed by operating personnel immediately in accordance with safety regulations, the Codex of the TS SR, the OI, and the LOR. An order from the operations service is not executed if it is unclear or evidently incorrect, and its execution could lead to a threat to human health or life or to extensive damage. In this case the operating staff must notify the operations service of this fact and ask for an explanation. However, if the individual issuing the central control order insists it be executed despite this warning, the given order must be executed after the proper entries have been made in operating logs and on a recording device. This, however, does not apply to cases where human health and life are at risk. The individual that insists on execution of the order takes full responsibility for the consequences.

Personnel working with sources and at substations must not, without permission from the relevant DSO central control facility, make changes to connections, perform tests, or change protection and automated equipment settings, make changes in control and information system databases, and on other equipment that is under central control. This does not include exceptional cases where there is a threat of significant material damage, or to human health or life. Production or electrical station personnel shall immediately inform the relevant dispatcher of the activities in these exceptional cases.

Prior to performing operating manipulation, the individual performing the manipulation must repeat the order to the ordering authority and then make a written record of the order. This record may replace that made by an automatic recording device in cases where this is so stipulated by the LOR.

# SOURCE OPERATION

An operator of equipment operating in parallel with the DS must keep it in perfect technical condition.

Switching elements, power elements, and protection must be, including pursuant to Decree of the Ministry of Labour, Social Affairs and Family of the Slovak Republic No 508/2009, functional and tested at regular intervals by qualified workers, and the results must be documented in an appropriate document. This document shall provide evidence of the chronology of the prescribed tests and shall be kept at the equipment of the source. It also certifies the proper functioning of the source.

The operator must give the DSO functional test report, technical inspection and test certificates (switching elements, protection, etc.) and other related documents upon request.

If needed, the DSO may require testing of protection devices for separation from the network and coupling switch protection. The DSO has the right to require the operator to change the source protection settings if required by DS operation.

Upon request by the DSO, the source operator must submit proof to the relevant power equipment operator of the part of the DS to which the source is connected that connected electrical equipment has been kept in commensurate technical condition; and technical inspection and test reports for equipment serving to feed power from the source, particularly on the functionality of protective devices and the main isolation point.

The source operator must allow access to the source’s switching element and its electrical protective devices.

When asked to do so by the DSO for necessary technical reasons, the source operator must disconnect the source.

In the case of danger or a fault, the DSO is entitled to immediately disconnect the source from the DS.

The source must not be connected to the DSO’s network (especially after a fault) until reconnection conditions pursuant to this document are met.

After coming to an agreement with the source operator, authorised DSO personnel must be given access to switching equipment, to measuring instruments and to protective devices.

The source operator must discuss intended changes with the DSO that may affect parallel operation with the network sufficiently in advance (for example, a change in source power output, replacement of protective devices, changes to compensation equipment, etc.). The DSO shall notify the source operator of substantial changes in its network that can affect parallel operation, for example an increase in short-circuit power.

If approval from the DSO CC is required for switching a source to the DS, the DSO will agree with the source operator on a section of the LOR where the personnel authorised to perform the switching are named. This part must also include a clause on fault signalling, disconnection signalling, and source equipment connection times.

Planned equipment outages must be properly prepared in all phases of operation preparations. The procedure for performing planned work is defined in the DSO’s operating instructions published on the company’s website.

In exceptional cases, within the scope of its operational authority, the DSO’s central control response service may permit the shutdown of equipment without prior planning, for work and repairs during fault elimination, as well as for extraordinary work when there is a danger due to delay or there is a health risk.

Prior to every planned shutdown of production equipment, or shutoff of equipment for work, the DS user who is responsible for the equipment’s operation must ask the DSO CC to agree with the equipment being taken out of operation.

ANNEX 4

Specifications for measuring electricity

Specifications for measuring electricity are regulated in detail by ‘Electricity Measurement Specifications’ on the DSO’s website.

A link to these guidelines is below:

https://www.vsds.sk/edso/domov/technicke-info/meranie-distribucie/suvisiace-dokumenty

or

https://www.vsds.sk/edso/domov/technicke-info/technicke-podmienky .