Series 0500 - Drainage Specification (formerly Series 0500) Revision 1

500 Introduction.

501 (mm/yy) Pipes for Drainage and for Service Ducts

502 Excavation for Pipes and Chambers

503 (mm/yy) Bedding, Laying and Surrounding of Pipes.

504 Jointing of Pipes

505 Backfilling of Trenches

506 Connecting to Existing Drains Chambers and Channels

507 (mm/yy) Chambers

508 Gullies and Pipe Junctions

509 Testing and Cleaning

510 Surface Water Channels and Drainage Channel Blocks

511 Land Drains

512 Backfilling to Pipe Bays and Verges on Bridges

513 Permeable Backing to Earth Retaining Structures

514 Fin Drains

515 Narrow Filter Drains

516 Combined Drainage and Kerb Systems

517 Linear Drainage Channel Systems

518 (mm/yy) Thermoplastics Structured Wall Pipes and Fittings

519 (mm/yy) Concrete Bagwork

520 (mm/yy) The Cleaning of Existing Drainage Systems

521 (mm/yy) Low Pressure High Volume Jetting of Drainage Systems

522 (mm/yy) Vortex Separators

523 (mm/yy) Grassed Surface Water Channels

524 (mm/yy) Combined Surface Water Channel and Pipe (Concrete)

525 (mm/yy) Reservoir Pavements

500 Introduction

1 (mm/yy) This Series is part of the Specification for Highways Works. Whilst this Series is particularly relevant to the subject matter in its title it must be read in conjunction with the general requirements in Series 000 and 100 and with other Series relevant to the specification of the particular works to be undertaken.

501 (mm/yy) Pipes for Drainage and for Service Ducts

General

1 (mm/yy) Where the term drain is used in this Series it shall be deemed to include the terms sewer and piped culvert.

(mm/yy) The Contractor shall design the piped culverts listed in contract specific Appendix 1/10 in accordance with the requirements of Clause 106 and this Series.

2 (mm/yy) All drains constructed of pipes as well as piped culverts up to and including 900 mm internal diameter shall comply with this Series and any additional requirements in contract specific Appendix 5/1. Drains constructed using pipes exceeding 900 mm internal diameter as well as box and piped culverts shall comply with Series 2500. Unless otherwise described in contract specific Appendix 5/1 only one type of pipe shall be used within any individual drain or service duct between consecutive chambers. The Contractor shall ensure that all drainage materials are not subjected to any form of deterioration before installation into the works.

Pipes for Drainage

3 (mm/yy) Pipes for drainage shall be selected from the alternatives in Table 5/1 titled Pipes for Drainage and shall comply with Clause 104 and contract specific Appendix 5/1. The Contractor shall demonstrate the pipes selected satisfy the hydraulic design of the system as described in contract specific Appendix 5/1. On completion of the whole of the drainage works, the Contractor shall provide the Overseeing Organisation with a schedule showing details of all pipe types used, including quality, joints and name of manufacturer. This will form the basis of a declaration of performance for the drainage.

Corrugated Steel Pipes

4 (mm/yy) Corrugated steel pipes shall be manufactured from either:

- (mm/yy) bolted segmental plate pipes complying with sub-Clause 6 of this Clause and having plate thicknesses as described in contract specific Appendix 5/1; or,

- (mm/yy) galvanized steel sheet suitable for lock seam fabrication complying with BS EN 10346 grade DX51D + Z600, or aluminium coated steel sheet complying with AASHTO specification M274-87.

(mm/yy) Corrugated steel pipes complying with (2) above shall be manufactured from steel of minimum thickness 1.25 mm unless otherwise described in contract specific Appendix 5/1.

5 (mm/yy) Where described in contract specific Appendix 5/1 corrugated steel pipes shall be provided with additional protection of hot applied bitumen complying with BS EN 13808, BS EN 15322 or BS EN 14023 having a minimum peak cohesion value of 1.0 J/cm2 by pendulum test in accordance with BS EN 13588.

6 (mm/yy) Bolted segmental plate pipes shall meet the following requirements:

- (mm/yy) Steel for the plates shall comply with BS 1449 : Part 1.1, Grade 3 or Grade 4, Condition HR;

- After forming, the depth of the corrugations shall be within a tolerance of ± 6% and the pitch of the corrugations within a tolerance of ± 4% of the nominal dimensions. Plates shall have a minimum lip of 45mm beyond each end crest. Cut edges shall be free from notches, gouges, rust or burrs;

- (mm/yy) Bolts and nuts for connecting plates shall comply with BS EN ISO 4014, BS EN ISO 4017 and BS EN ISO 4032, for BS EN ISO 898-1 and 'BS EN 20898-2, ISO 898-2' property class 8.8, nominal size M20; or with BS 4395 : Part 2, nominal size M20; or with BS EN ISO 898-1 and 'BS EN 20898-2, BS EN ISO 898-2' property class 10.9;

- (mm/yy) When all the plates have been assembled, the nuts shall be tightened against a domed washer. The tightening shall be repeated if necessary to achieve the torque recommended by the manufacturer; and,

- Steel plate shall be galvanized in compliance with Clause 1909. Plates shall be galvanized after forming the corrugations and completing all necessary cutting, punching and drilling. Units in which the zinc coating has been burned by welding or otherwise damaged in fabrication, transport or handling at site shall be made good in compliance with Clauses 1907 and 1908. Bolts and nuts shall be galvanized in compliance with Clause 1909.

Table 5/1 Pipes for Drainage

| Material | Usage | Standard | Particular Requirements |
| --- | --- | --- | --- |
| Vitrified clay | Foul drains | BS EN 295 |  |
|  | Surface water drains | BS EN 295 |  |
|  | Filter drains | BS EN 295 |  |
| Concrete (With Portland cement or sulfate-resisting cement when required in contract specific Appendix 5/1. Supersulfated cement shall not be used) | Foul & surface water drains | BS 5911-1 and BS EN 1916 (Ordinary reinforced or unreinforced) BS 5911-5 |  |
|  | Surface water drains | BS 5911-1 |  |
|  | Filter drains | BS 5911-1 (Porous with ogee or rebated joints) |  |
|  |  | BS 5911-1 | Unperforated not exceeding 2 m in length with open joints or castellated rebated joints with the total slot area between castellations being at least 1000 mm² per metre length of pipe OR Perforated with circular holes not greater than 10 mm nor less than 3 mm in diameter |
| Glass reinforced plastics (GRP) | Foul & surface water drains | BS EN 14364 | Class to be as specified in contract specific Appendix 5/1 |
| Iron | Foul & surface water drains | BS 437 (Cast iron) BS EN 598 (Ductile iron) |  |
| Thermoplastics solid wall pipes and fittings Unplasticised polyvinyl-chloride (PVC-U) Polypropylene (PP) Polyethylene (PE) | Foul & surface water drains | BS 4660 or BS 5481 or BS EN 1401 (PVC-U) BS EN 1852-1 (PP) BS EN 12666-1 (PE) | See the UK national forward to the relevant BS EN. The grade appropriate for use without structural calculations shall be used i.e. SN8 for PP & PE and SN4 (SDR 41) for PVC-U |
|  | Filter drains | BS EN 13598 (BS 4660 for cleaning eyes) or BS EN 1401 (PVC-U) BS EN 1852-1 (PP) BS EN 12666-1 (PE) | Perforated with not less than 1000 mm² of holes per metre length of pipe. The perforations shall not reduce the pipe stiffness by more than 5%. Circular perforations not greater than 10 mm nor less than 3 mm in diameter or rectangular slots not greater than 4 mm nor less than 0.6 mm in width |
| Thermoplastics structured wall pipe and fittings | Surface water drains | Clause 518 | Unperforated with watertight joints and with a pipe stiffness class, creep ratio and impact resistance as described in contract specific Appendix 5/1 |
|  | Filter drains | Clause 518 | Perforated with not less than 1000 mm2 of holes per metre length of pipe. The perforations shall not reduce the pipe ring stiffness by more than 5 %. Circular perforations not greater than 10mm nor less than 3 mm in diameter or rectangular slots not greater than 4 mm nor less than 0.6 mm in width |
|  | Subsoil field drains | BS 4962 or Clause 518 |  |
| Corrugated steel | Surface water drains, filter drains | BS EN 10346 AASHTO Designation: M27 4-87 (2012) |  |

Pipes for Service Ducts

7 (mm/yy) Pipes for service ducts, excluding those in use in highway communications installations, shall be selected from the alternatives in Table 5/2 and shall comply with the standards and particular requirements therein. Pipes for use in highway communications installations shall comply with Series 1500. Pipes for service ducts shall have a smooth internal bore without any sharp edges to the ends of pipes, shall comply with contract specific Appendix 5/2, and be of 100 mm internal diameter unless otherwise described therein. Their alignment shall be tested in accordance with sub-Clause 509.9.

The use of pipes and fittings other than those included in Table 5/2 shall be permitted provided that they hold current Product Acceptance Scheme certification in accordance with sub-Clauses 104.15 and 104.16 stating that they are a suitable alternative to those listed in Table 5/2.

Table 5/2 Pipes for Ducts

| Material | Standard | Particular Requirements |
| --- | --- | --- |
| Vitrified clay | BS EN 295 | Plain-ended, self-aligning flexible sleeve jointed with internal ends radiused to 3 mm minimum |
| Iron | BS EN 598 (Ductile iron) |  |
| Glass reinforced plastics | BS EN 14364 | Class to be as specified in contract specific Appendix 5/2 |
| Thermoplastics solid wall Unplasticised polyvinyl-chloride Polypropylene (PP) Polyethylene (PE) | BS 4660 and BS EN 13598 or BS 3506 (Class C) or (PVC-U) BS EN 1401, BS EN ISO 1452-1 to 5 as appropriate class PN10. BS EN 1852-1 (PP) BS EN 12666-1 (PE) | When pipes BS 3506 (Class C) are used, joints shall comply with BS EN ISO 1 452-1 to 5 as appropriate Thermoplastics single wall (Restricted to ducts buried a minimum of 600 mm below the surface) BS EN 61386-24 Ducts to BS EN 61386-24 shall be classified as normal duty, corrugated have a degree of protection against ingress of foreign objects classification rating of 3 or 4 and a degree of protection against ingress of water classification rating of 7. Resistance to bending requirements shall be as stated in contract specific Appendix 5/2 |
| Thermoplastics structured wall | BS EN 61386-24 and Clause 518 | Ducts to BS EN 61386-24 shall be classified as normal duty, corrugated have a degree of protection against ingress of foreign objects classification rating of 3 or 4 and a degree of protection against ingress of water classification rating of 7. Resistance to bending requirements shall be as stated in contract specific Appendix 5/2. |

8 Each duct shall be fitted with a pigmented, stranded polypropylene or equivalent rot-proof material draw rope of 5 kN breaking load and having a design life of not less than 20 years, the ends of which shall be either made fast to marker blocks as shown on HCD Drawing Number I1 or secured inside chambers. The ends of a duct shall be either sealed by removable stoppers immediately it has been laid, or terminated in chambers of the type specified in contract specific Appendix 5/2.

502 Excavation for Pipes and Chambers

1 Excavation shall comply with Clause 602 and with the following:

- (mm/yy) soft spots existing below the bottom of an excavation shall be removed and the resulting voids backfilled with Type 1 unbound mixture for subbase complying with Clause 803 or pipe bedding material complying with Clause 503, both well compacted, or ST1 concrete in compliance to Clause 2602;

- any additional excavation below the bottom of an excavation that is required because the Contractor has allowed the bottom to become soft or otherwise unacceptable for the construction of the pipeline or chambers shall be made good as described in sub-Clause 1(i) of this Clause;

- any excavation greater than the net volume required for the permanent works below the level of any pipe surround shall be made good as described in (i) above.

2 Unless otherwise described in contract specific Appendix 5/1, all pipes in or under new embankments shall be laid only when the embankment has been formed and compacted to formation level under paved areas, to finished earthworks level in other areas, or to a level which will give a minimum cover of 1.2 m to the pipes, whichever is the lowest.

503 (mm/yy) Bedding, Laying and Surrounding of Pipes

1 Immediately following the excavation of the trench, the pipes shall be laid and jointed on the pipe bed.

Pipes shall be laid so that each one is in contact with the bed throughout the length of its barrel. The pipes shall be laid at the level and gradients shown on the drawings and schedules. The deviation in level from that specified at any point shall not exceed 20 mm and in addition the algebraic difference of the deviation in level at any two points on each pipe shall not exceed 30 mm. In the case of socketed or sleeve jointed pipes the bed shall be cut away and removed at each socket or sleeve to give a clearance of at least 50 mm, or 100 mm for trenches in material designated as hard material, so that the socket or sleeve does not bear on the bed. Pipes shall be laid on setting blocks only where a concrete bed or cradle is used.

Pipes and fittings that show any sign of damage shall be excluded from the works. The pipes and fittings' joint surfaces and components shall be cleaned immediately before laying. Measures shall be taken to prevent soil or other material from entering pipes, and to anchor each pipe to prevent movement before the work is complete.

2 Pipes complying with BS 4962 which are corrugated coilable perforated pipes shall, unless otherwise permitted in contract specific Appendix 5/1, be laid only by automatic single pass drain laying machines.

3 (mm/yy) Drainage pipe and bedding combinations shall be selected from the alternatives described in contract specific Appendix 5/1. The granular material shall consist of natural and/or recycled coarse aggregate complying with BS EN 13242 and have a declaration of performance for its intended use, the declaration of performance shall demonstrate that the aggregate meets the specification.

Where recycled coarse aggregate is used in this Clause, it shall have been tested in accordance with Clause 710 and shall not contain more than 1% 'other' materials (Class X). Pipe bedding, haunching and surrounding material shall be as shown on HCD Drawing Numbers F1 and F2, and shall comply with the following:

- (mm/yy) For pipes on beds shown on HCD Drawing Numbers F1 and F2 as Types B, F, S, I, J, L, K and M the aggregate shall have:

  - (mm/yy) geometrical requirements in accordance with Table 5/3;

  - (mm/yy) a resistance to fragmentation in Category LA50 in accordance with BS EN 13242, clause 5.2 and table 9;

  - (mm/yy) a water-soluble sulfate content of less than 0.2% category SS0.2 in accordance with BS EN 13242 when tested in accordance with BS EN 1744-1, clause 10;

  - (mm/yy) all other requirements in Category NR.

- (mm/yy) For pipes on beds shown on HCD Drawing Number F1 as Types N and T the aggregate shall comply with the geometrical requirements of either Table 5/3 or with Table 5/4, and with the fragmentation, watersoluble sulfate content and other requirements of (i) above.

- (mm/yy) For pipes on beds shown on HCD Drawing Number F1 as Types A and Z concrete shall be ST4 and ST2 respectively, in compliance to Clause 2602. Backfilling shall not be carried out until after the concrete has cured. The concrete bed or surround may extend to the sides of the trench. Class 8 material shall be used to fill any voids formed.

- Except for filter drains a further surround above the bed, haunch and surround described above shall be provided to a height of 300 mm above the top of the pipe consisting of Class 8 lower trench fill material as described in Table 6/1 and in compliance with Series 600.

- Unless otherwise described in contract specific Appendix 5/1 the materials used for the bedding, haunching and surrounding of filter drains shall comply with the appropriate bedding, haunching and surrounding materials specified in sub- Clauses 503.3.(i) to 503.3.(iv) and with the requirements for backfilling specified in sub-Clause 505.3.

- Pipes shown on HCD Drawing Number F2 shall be laid with slots or perforations upwards where a concrete bed is used. For other beds the slots or perforations shall be orientated as described in contract specific Appendix 5/1.

Table 5/3 Coarse aggregate for pipe bedding, haunching and surrounding material

| BS EN 13242, Coarse aggregate |  |  |
| --- | --- | --- |
| Category for general grading requirements | G 80-20C |  |
| Category for tolerances at mid-size sieves | GT NR |  |
| Category for maximum values of fines content | Natural aggregate - f1.5 manufactured aggregate, recycled aggregate - f4 |  |
| Nominal pipe diameter, mm | Aggregate size, mm |  |
|  | Graded | Single |
| Not exceeding 140 | - | 4/10 |
| Exceeding 140 but not exceeding 400 | 2/14 or 4/20 | 4/10, 6/10 or10/20 |
| Exceeding 400 | 2/14, 4/20 or 4/40 | 4/10, 6/14,10/20 or 20/40 |

Table 5/4 Fine and all-in aggregated for pipe bedding, haunching and surrounding material

| BS EN 13242, Fine and all-in aggregate |  |  |
| --- | --- | --- |
|  | Fine | All-in |
| Category for general grading requirements | Category GF 80 | Category GA 80 |
| Category for tolerances on manufacturer's declared typical grading | GTF NR (no requirement) | GTA NR (no requirement) |
| Category for maximum values of fines content | Natural aggregate - f3 Manufactured aggregate, recycled aggregate - f10 | Natural aggregate - f3 Manufactured aggregate, recycled aggregate - f12 |
| Nominal pipe diameter, mm | Aggregate size, mm |  |
|  | Fine | All-in |
| Not exceeding 140 | 0/1, 0/2, 0/4or 0/6 | 0/10 |
| Exceeding 140 but not exceeding 400 |  | 0/10 or 0/20 |
| Exceeding 400 |  | 0/10, 0/20 or 0/40 |

4 (mm/yy) Materials for bedding, haunching and surrounding pipes within 500mm, or any other distance described in contract specific Appendix 5/1, of concrete, cement bound materials, other cementitious materials or stabilised capping shall comply with the requirements stated in sub-Clause 601.16.

5 (mm/yy) Materials for bedding, haunching and surrounding pipes placed within 500mm, or any other distance described in contract specific Appendix 5/1, of metallic structural elements shall comply with the requirements stated in sub-Clause 601.17.

6 (mm/yy) Except where the pipeline is to be tested in compliance with Clause 509 before backfilling as specified in contract specific Appendix 5/1, the completion of the bedding, haunching and surrounding of the pipes is to be carried out immediately after jointing. The bed, haunch and surround shall be brought up equally on both sides of the pipe ensuring that it is in contact with the underside of the pipe barrel and be carefully compacted in layers not exceeding 150 mm thickness ensuring full compaction next to the trench walls. Pipes shall be maintained to line and level during the bedding, haunching and surrounding operations.

Where pipelines are to be tested before being covered the bedding haunching and surrounding material shall only be brought up sufficiently to support the pipeline and the joints shall be left exposed until the test is completed satisfactorily.

7 (mm/yy) Duct construction shall comply with the requirements of contract specific Appendix 5/2.

504 Jointing of Pipes

1 Rigid joints shall mean joints made solid by caulking the sockets, or bolting together flanges integral with the pipes. Flexible joints shall mean joints made with deformable rings or gaskets held between pipe spigots and sockets, sleeves or collars.

2 Joints in surface water drains shall be watertight complying with Table 5/1 or partly watertight complying with Table 5/1 as described in contract specific Appendix 5/1. Foul drains shall have watertight joints. Filter drains shall have joints complying with Table 5/1. Ducts need not have watertight joints unless otherwise described in contract specific Appendix 5/2.

3 (mm/yy) Watertight joints shall comply with Table 5/1, the manufacturer's instructions and the following:

- Rigid joints shall be used only where permitted in contract specific Appendix 5/1. Spigots and sockets of rigid joints jointed conventionally and the socket completely filled with mortar designation (i) complying with Clause 2404, excluding lime; a fillet of mortar being worked around the socket extending for a length of not less than 50 mm from the face of the socket.

- Joints in PVC-U pipes shall not be made with plastic solvent.

- Flexible mechanical joints may be used with surface water pipes complying with BS EN 295.

- (mm/yy) Joints for cast iron pipes to BS 437 shall comply with BS EN 877 and have a declared performance that meets the specification requirements.

- Joints in thermoplastics structured wall pipe shall comply with Clause 518.

4 (mm/yy) Partly watertight joints for surface water drains shall be tested in accordance with sub-Clause 509.9 and shall be in accordance with Table 5/1. Push fit joints shall have a register to ensure that the pipe is fully pushed into the joint.

Corrugated steel pipes of lock seam fabrication, not exceeding 900mm internal diameter, shall be joined in accordance with the manufacturer's instructions. Bolted segmental plate pipe arches or circular pipes, not exceeding 900mm internal diameter, shall be joined in accordance with sub-Clause 501.6 (iv) and the manufacturer's instructions.

5 Where a concrete bed, cradle, arch or surround is used with rigid pipes having flexible joints, joint filler board complying with Clause 1015 shall be placed in contact with the end of the socket at a pipe joint and shall extend through the full thickness of the concrete in contact with the pipe. Such joints in the concrete bed, haunch or surround shall be at intervals not exceeding 5 metres except where the spacing of joints in the pipe exceeds 5 metres when they shall be at each pipe joint.

6 (mm/yy) Joints in pipes for filter drains shall comply with Table 5/1 and with the following:

- Non-porous and unperforated concrete and clay pipes with spigot and socket, rebated or ogee joints shall be laid with unsealed joints and with a gap of 10 mm between the end of the pipe and the inner end of the socket or rebate. The pipes shall be supported by a jointing material within the sockets over the lower third of the circumference so that there are no vertical steps between one pipe and another. Such pipes shall only be used with Type B filter material as described in Clause 505.

- The ends of perforated or porous concrete pipes with rebated joints and perforated clayware pipes with rebated or with flexible sleeve joints shall be pushed tightly together.

- Perforated or slotted thermoplastics pipes with spigots and sockets or sleeves may be dry-jointed or jointed as described in sub-Clauses 3 and 4 of this Clause.

- Other perforated pipes shall be jointed as unperforated pipes of the same material.

7 Joints in pipes for service ducts shall comply with BS 4660, BS EN 13598-1 and with the following:

- Pipes for ducts shall be jointed so that no silt, grit, grout or concrete surround is able to enter the duct. Pipes with push-fit joints shall have a register to ensure that the pipe is fully pushed into the joint.

- (mm/yy) Joints in pipes to BS 3506 shall comply with BS EN ISO 1452-1 to 5 as appropriate.

505 Backfilling of Trenches

1 Backfilling shall be undertaken immediately after the required operations preceding it have been completed.

2 Except where otherwise described in contract specific Appendix 5/1, trenches other than filter drain trenches shall be backfilled above the pipe surround material described in Clause 503, with Class 1, 2, or 3 general fill material complying with Series 600.

3 (mm/yy) Where detailed in contract specific Appendix 5/1 the bases of trenches formed on water soluble soils shall be sealed with a waterproof geotextile membrane. The geotextile membrane shall be in accordance with Clause 609.

(mm/yy) Each side of the waterproof geotextile membrane shall be protected by a layer of non-woven geotextile. The non-woven geotextile shall be in accordance with Clause 609.

4 (mm/yy) Sub-base material for the upper layer of the drain shall consist of Type 1 material to Clause 803.

5 (mm/yy) Geotextile membranes used between the upper and lower section of combined surface and sub-surface drains shall be in accordance with Clause 609.

6 (mm/yy) Use of lightweight aggregates as filter material shall be subject to the approval of the Overseeing Organisation.

7 (mm/yy) Filter drains shall be backfilled as described in contract specific Appendix 5/1 with Type A, Type B or Type C filter material which shall consist of natural or recycled coarse aggregate complying with BS EN 13242 and the following:

- for Type A and C, grading requirements for unbound mixtures in accordance with Table 5/5 and BS EN 13285;

- for Type B, geometrical requirements in accordance with Table 5/5 and BS EN 13242;

- a resistance to fragmentation in Category LA50 in accordance with BS EN 13242, clause 5.2 and table 9;

- (mm/yy) a water-soluble sulfate content of less than 0.2% Category SS0.2 in accordance with BS EN 13242 when tested in accordance with BS EN 1744-1, clause 10;

- all other requirements in Category NR.

Where recycled coarse aggregate is used in accordance with this Clause, it shall have been tested in accordance with Clause 710 and shall not contain more than 1% 'other' materials (Class X).

Table 5/5: (mm/yy) Grading and geometrical requirements for filter drain material

|  | Type A | Type B | Type C |
| --- | --- | --- | --- |
| Standard | BS EN 13285 | BS EN 13242 | BS EN 13285 |
| Size, mm | 0/20 | 20/40 | As described in contract specific Appendix 5/1 |
| Grading | GE (with an additional sieve) | GC80-20 |  |
| Oversize category | OC80 |  |  |
| Category for tolerances at mid-size sieves |  | GTNR (no requirement) |  |
| Category for maximum fines | UF3 | FNR (no requirement) |  |
| Summary grading requirements |  |  |  |
| Sieve size, mm | Percentage by mass passing |  |  |
| 80 63 40 20 10 4 2 0.500 0.125 0.063 | 100 80 - 99 50 - 90 30 - 75 15 - 60 0 - 35 0 - 4 0 - 3 | 100 98 - 100 80 - 99 0 - 20 0 - 5 | As described in contract specific Appendix 5/1 |
| % in size fraction |  |  |  |
| 4/10 | 5-35 |  |  |
| 2/4 | 5 - 35 |  |  |

Filter materials, shall be tested for permeability in accordance with sub-Clause 509.8 and shall comply with permeability requirements as described in contract specific Appendix 5/1.

Locations where Type A material is to be used shall be as specified in contract specific Appendix 5/1.

8 (mm/yy) Materials for backfilling trenches and filter drains placed within 500mm, or any other distance described in contract specific Appendix 5/1, of concrete, cement bound materials, other cementitious mixtures or stabilised capping shall comply with the requirements stated in sub-Clause 601.16.

9 (mm/yy) Materials for backfilling trenches and filter drains placed within 500mm, or any other distance described in contract specific Appendix 5/1, of metallic structural elements shall comply with the requirements stated in sub-Clause 601.17.

10 (mm/yy) Backfilling shall be deposited and compacted in compliance with Clause 612. Filter material for filter drains shall be deposited in layers not exceeding 225 mm loose depth; each layer being compacted in compliance with Table 6/4 Method 3.

11 (mm/yy) Material shall be deposited in even layers and shall not be heaped in the trench before being spread. Spreading and compaction shall be carried out evenly without dislodging, distorting or damaging the pipe. Power rammers shall not be used within 300 mm of any part of the pipe or joint.

12 (mm/yy) Except in carriageways, other paved areas and locations described in contract specific Appendix 5/1, backfill of trenches shall be brought up to ground level. Where topsoil is at the surface on the line of the trench the upper section of the backfill shall be topsoil of the thickness described in contract specific Appendix 6/8, or of the same thickness and quality of topsoil as the surrounding ground where no thickness is specified. For trenches in carriageways or other paved areas the backfill shall be brought up to formation level, or sub-formation level where capping is required, unless a lower level is described in contract specific Appendix 5/1. Sheeting and other excavation supports shall be removed as the filling proceeds unless otherwise described in contract specific Appendix 6/3.

13 (mm/yy) The position of service ducts shall be marked when the trenches are backfilled and permanent marker blocks and location posts provided as described in contract specific Appendix 5/2.

Bitumen bound shredded tyres

(mm/yy) If the use of bitumen bound shredded tyres is proposed as a treatment to improve the stability of combined surface and sub-surface drains then the specification is to be submitted to the Overseeing Organisation for approval prior to use.

506 Connecting to Existing Drains Chambers and Channels

1 Where described in contract specific Appendix 5/1, existing drains shall be extended, connected and jointed to new drains, chambers or channels. All such connections shall be made during the construction of the new drain or other work and their positions recorded by the Contractor who shall provide to the Overseeing Organisation a copy of the record of the connections made the previous day.

Where pipe connections are made to existing brick concrete or stone drains, chambers or channels, the pipes shall be well and tightly built into the concrete, brick or masonry work and be so placed as to discharge at an angle not greater than 60° to the direction of flow of the drain or channel and with the end of the pipe carefully cut to the necessary angle. Where the connections are between pipe drains, special connecting pipes shall be laid and jointed as described in contract specific Appendix 5/1.

2 Before entering or breaking into an existing sewer or drain, the Contractor shall give notice of his intention to do so to the authority responsible for the drainage system to which the connection is to be made.

3 (mm/yy) Unless otherwise stated in contract specific Appendix 2/2, existing drains no longer required shall, as required by contract specific Appendix 5/1, be sealed with ST2 concrete, in compliance with Clause 2602, or removed and replaced with general fill material complying with Clause 601 and Table 6/1 and compacted in compliance with Clause 612, or grouted with a 1:10, cement: pfa mix.

The grout shall use the minimum quantity of water to ensure the fluidity necessary to render it capable of being pumped to the ends of the pipe and be in accordance with the manufacturer's instructions. It shall be used within one hour of mixing but when the mix contains a retarding admixture this time may be extended in accordance with the manufacturer's instructions. The cement shall comply with BS EN 197-1 and the pulverised fuel ash (pfa) with BS 3892 : Part 2, fineness to Zone B and sulfate content not exceeding 1.5%.

507 (mm/yy) Chambers

1 (mm/yy) Chambers shall include manholes, catchpits, inspection chambers, draw pits and walled soakaways. Chambers shall be of the type specified in contract specific Appendix 5/1, constructed in accordance with HCD Drawing Numbers F3 to F12 and F25 to F27 as appropriate to that type.

Chambers for use in highway communications installations shall comply with Series 1500. All ST concrete referred to in this Clause shall comply with Clause 2602, unless otherwise described in contract specific Appendix 5/1.

2 (mm/yy) Foundations to chambers shall be of ST4 concrete. Channels for chambers shall be formed and finished smooth in the foundation concrete or constructed of preformed half circle channels, with sides benched in ST4 concrete, or mortar designation (i) complying with Clause 2404 excluding lime.

Alternatively for inspection chambers not exceeding 1.3 metres in depth to invert, complete plastics units or other units in equivalent material surrounded by 150 mm of ST4 concrete may be used.

3 Brickwork shall comply with Series 2400 and be built with mortar designation (i) in English bond. The joints of brickwork where exposed shall be finished as specified for unpointed joints in Clause 2412. The ends of all pipes shall be neatly built into the brickwork and finished flush with mortar designation (i). Where precast concrete adjusting units are used they shall conform to BS EN 1917 and BS 5911-3.  Benching width for chambers detailed on HCD drawing numbers F25 to F27 shall be 300mm for branch connection.

4 (mm/yy) Precast concrete chambers shall comply with BS 5911-3 and BS EN 1917 and the particular requirements described in contract specific Appendix 5/1. Cast in-situ concrete chambers shall be constructed of ST4 concrete complying with Clause 2602 and the particular requirements described in contract specific Appendix 5/1.

5 (mm/yy) Corrugated galvanized steel chambers shall comply with Clause 501 with in situ ST4 concrete inverts and precast concrete cover slabs complying with BS 5911-3 and BS EN 1917 and the particular requirements described in contract specific Appendix 5/1. They shall be surrounded with well graded granular material Class 6M as described in Table 6/1 compacted in accordance with Clause 612.

6 (mm/yy) Where the depth of invert of chambers, excluding inspection chambers, exceeds 900 mm below the finished surface of the carriageway or the adjacent ground, chamber steps complying with BS EN 13101 shall be built in accordance with relevant Series F-HCD Drawings. The steps shall have a declaration of performance for their intended use within the permanent works. Threaded components shall be galvanised in compliance with Clause 1909.

7 (mm/yy) Excavation around chambers, except those described in sub-Clause 5 of this Clause, shall be backfilled with general fill material as described in Table 6/1 and compacted in compliance with Clause 612. Where mechanical compaction is impracticable, the excavation shall be backfilled with ST2 concrete. Where there are precast concrete access shafts to precast concrete chambers, the shafts shall be surrounded by a minimum thickness of 150 mm of ST4 concrete, and the remaining excavation backfilled with general fill material as described in Table 6/1 compacted in compliance with Clause 612.

8 Chambers for foul drains shall be tested for water tightness in accordance with Clause 509 and where required in contract specific Appendix 5/1.

Table 5/6 Length of articulated pipe

| Nominal Pipe Diameter (mm) | Length of Pipe (mm) |
| --- | --- |
| 450 and less | 500 to 750 |
| Greater than 450 | 750 to 1000 |

9 For all pipelines except those constructed with corrugated pipes the nearest joint to any chamber shall be not more than 500 mm from the inner face of the wall and shall not be restricted by any concrete.

Between this and the next joint, the length of the articulated pipe shall be in accordance with Table 5/6.

10 (mm/yy) Chamber covers, gratings and frames shall be as described in contract specific Appendix 5/1 and shall comply with BS EN 124: 1994 and sub-Clauses 11 and 20 of this Clause.

The cover shall be of suitable material, design and construction to achieve the required in-service skid resistance potential determined by the accelerated polish test method described in BS 9124. The Polished Skid Resistance Value (PSRV) shall be as stated in contract specific Appendix 5/1.

The Unpolished Skid Resistance Value (USRV) is not an acceptable alternative to demonstrate in-service skid resistance.

11 Class D 400 units and above shall incorporate a permanent non-rock feature either triangular point suspension or machined faces. Where a cover is required to be seated in a frame the design life of the seating shall match that of the frame. The seating shall not reduce the performance characteristics of the frame and cover.

12 Unless otherwise specified in contract specific Appendix 5/1, chamber covers shall have the following minimum clear opening requirements:

- Rectangular frame 600mm, with a minimum diagonal measurement of 700mm; 8.15.2

- Circular frame minimum diameter of 700mm.

13 Vents are not required in chamber covers unless otherwise stated in contract specific Appendix 5/1.

14 Where stated in contract specific Appendix 5/1 the sealing of a cover within the frame is required.

15 Access covers with a clear opening of greater than 1m shall comply with BS 9124.

16 (mm/yy) Bolts supplied for loosely coupling separate sections of covers and gratings shall be steel hexagon headed, complying with the requirement of BS EN ISO 4016, BS EN ISO 4018 and BS EN ISO 4034 and be galvanized in compliance with Clause 1909. They shall not be less than size M16 complete with hexagon nut and shall be provided with means to prevent undue tightening of unit sections.

(mm/yy) Where pins or circlips are used as part of the securing device these shall be of equal cross-sectional area.

17 Unless otherwise specified in contract specific Appendix 5/1, all covers, gratings and frames shall be supplied in a fine cast (uncoated) condition. Where a coating is specified in contract specific Appendix 5/1, the coating shall only be applied when the surfaces of the casting are clean, free from rust and dry.

18 Requirements for special duty covers for use in carriageways shall be as described in contract specific Appendix 5/1.

19 Gratings for catchpit chambers shall have a minimum waterway area as described in contract specific Appendix 5/1.

20 Two sets of lifting keys shall be delivered to the Overseeing Organisation for each type of cover supplied. At least two keyways, as detailed on HCD Drawing No. F17, shall be provided in each complete cover, one in each segment for segmental covers. A recess for a prising bar shall be incorporated in manhole covers unless other means of loosening the cover from the frame are provided.

21 Frames for chamber covers and gratings shall be set in cement mortar designation (i) complying with Clause 2404 or a quick setting mortar of equivalent strength with a declaration of performance for its intended use. The declaration of performance shall be submitted to the Overseeing Organisation.

(mm/yy) Chamber tops and gully tops shall be bedded upon material which has the following properties:

- non-shrinkable;

- a minimum workable life of 15 minutes;

- a compression strength that exceeds 30 N/mm2 within 3 hours of placing; and

- a tensile strength that exceeds 5 N/mm2 within three hours of placing.

22 (mm/yy) The bedding beneath the chamber top or gully top frame shall be free of voids.

(mm/yy) Packing materials shall not be used in the bedding of chamber tops and gully tops.

23 Where the adjustment or replacement of existing frames and covers or gratings is required, the units shall be taken up and re-fixed or removed and replaced with new units complying with sub-Clauses 10 to 20 of this Clause, or as described in contract specific Appendix 5/1. On taking up or removal of the unit, any concrete or mortar bedding shall be broken out and the surface prepared.

Where existing frames and covers or gratings are to be adjusted, the Contractor shall take up the unit and clean it so it is free from existing mortar, any debris, rust and is dry before re-use. The adjusted or replaced units shall be laid on a mortar bed complying with sub-Clause 21 of this Clause. The finished thickness of the mortar bed shall be between 10 mm and 25 mm. Where required in contract specific Appendix 5/1, covers and gratings shall be bedded using a quick setting high strength mortar with a declaration of performance for its intended use. The declaration of performance shall be provided to the Overseeing Organisation before use.

Unless otherwise described in contract specific Appendix 5/1, adjusted or replaced frames and covers or gratings shall be set flush with the new or reinstated surface. Any additional adjustments shall be by modifying the brickwork, or adjusting units in accordance with BS EN 1917 and BS 5911-3, in compliance with sub-Clause 507.3 or by using a frame of a suitable depth. On completion of the works, each cover shall be lifted and the frame and seating cleaned.

(mm/yy) Seatings of covers within frames shall have been manufactured to ensure that, when trafficked, stability and quietness are achieved in accordance with BS EN 124: 1994.

(mm/yy) The frame bearing area shall have the following properties:

- the nominal bearing pressure in relation to the test load in BS EN 124:1994;

- frames have an overall minimum bedding width of 50 mm of metal and a maximum overall bedding width of 120 mm of metal;

- for openings with corners, the external corners of the frame are solid (unless test data are provided that demonstrate the inclusion of holes does not reduce the structural integrity of the system) and may be square, curved or chamfered but at no point shall the width be less than the minimum bedding width.

(mm/yy) The bedding flange shall have a minimum thickness of 5 mm.

(mm/yy) Where vertical frame stiffening webs/gussets are provided, they shall be located adjacent to seatings.

(mm/yy) The tops of such triangular webs/ gussets shall be in accordance with BS 7903.

(mm/yy) There shall be no holes within the seating areas of the bedding flanges beneath the cover seatings.

(mm/yy) Any holes within flanges within the bedding area of the frame shall be minimal and not reduce the specified bearing area of the frame.

Placing of Frames and Covers

(mm/yy) The frame of chamber tops and gully tops shall be placed on the bedding material so that all webs of the frame are fully supported by the frame supporting structure.

(mm/yy) The bedding surface shall permit a bedding thickness of between 10 mm and 75 mm.

(mm/yy) The webs of the frame shall not overhang the internal faces of the frame supporting structure.

(mm/yy) Any holes within the frame shall be infilled with bedding material and the flanges of the frame enveloped by a minimum thickness of 10 mm of the same material.

(mm/yy) Exposed surfaces of the bedding material around the outside of the chamber or gully top frame shall be floated to fill any voids and remove loose fragments.

(mm/yy) The exposed surface of the bedding material inside the chamber shall be pointed to a smooth finish.

(mm/yy) Surround materials shall only be placed in contact with the frame once the bedding material has set.

Placement of Cover Surround Materials

(mm/yy) Where a self-setting fill material is used this shall be placed no higher than 40mm below the finished surface level.

Securing Chamber Covers and Frames

(mm/yy) Chamber covers and frames shall be secured to ensure that they are not dislodged by a vehicle.

Reinstatement Works

Frame Supporting Structure

(mm/yy) Where rebuilding involves more than one course of brickwork or precast concrete cover frame seating ring, an adjusting course shall be used to meet the specified finished surface level.

(mm/yy) Frame supporting structure reconstruction shall be engineering bricks in compliance with Clause 2400 (without holes or frogs) or adjusting units in accordance with BS EN 1917 and BS 5911-3, bedded on mortar that achieves a compressive strength exceeding 20 N/mm2 Class Md in accordance with BS EN 998 and Clause 2404 before loading.

Re-bedding of Covers/Gully Gratings

(mm/yy) Mixing and placing of proprietary bedding materials shall be in accordance with the manufacturer's instructions.

(mm/yy) Site made mortar shall be in accordance with Clause 2404.

(mm/yy) Bedding layers greater than 50 mm thick shall be placed in two stages.

(mm/yy) The first layer of the mortar shall be no thicker than 40 mm.

Reinstatement of Surrounding Flexible Carriageway

(mm/yy) There shall be no contact between any compaction device and the frame or cover to avoid damaging the frame, cover or the bedding layer.

(mm/yy) The joint between the reinstated and existing materials shall be sealed with bituminous material in compliance with clause 903.22.

508 Gullies and Pipe Junctions

1 (mm/yy) Gullies shall be trapped, untrapped or sumpless as described in contract specific Appendix 5/1 and be in accordance with HCD Drawing Numbers F13 and F14.

All ST concrete referred to in this Clause shall comply with Clause 2602 unless otherwise described in contract specific Appendix 5/1.

2 Gullies shall be constructed so that no part of the spout or trap has a cross-sectional area less than 2/3rd that of the outlet. The depth of water seal in trapped gullies shall be not less than 50 mm.

3 (mm/yy) Precast concrete gullies and cover slabs shall comply with BS 5911-6 and clay gullies with BS EN 295. In situ concrete gullies shall be as described in contract specific Appendix 5/1 and constructed of ST4 concrete of 150 mm minimum thickness, using permanent or removable shuttering.

(mm/yy) When constructing an in situ sumpless gully, the pot shall not distort under pressure.

Where in situ concrete gullies are formed with permanent shuttering, such shuttering shall have current product acceptance scheme certification in accordance with sub-Clauses 104.15 and 104.16.

4 Gully gratings, kerb type gully covers and frames shall comply with BS EN 124: 1994 and the following and shall be of the classes and sizes described in contract specific Appendix 5/1.

5 (mm/yy) The upper surface of gully gratings shall be flat except where otherwise described in contract specific Appendix 5/1.

Slots in gratings or between gratings and frames shall not be orientated parallel to the direction of traffic except where the slots are less than 150 mm long or less than 20 mm wide. Minimum waterway areas shall be as specified in contract specific Appendix 5/1. Unless otherwise specified in contract specific Appendix 5/1, all gratings and frames shall be supplied in a fine cast (uncoated) condition. Where a coating is specified in contract specific Appendix 5/1, the coating shall only be applied when the surfaces of the casting are clean, free from rust and dry. Frames shall be bedded on mortar complying with sub-Clause 507.21. Brickwork shall comply with sub-Clause 507.3.

6 (mm/yy) Backfilling to precast gullies shall be carried out up to sub-formation level with general fill material Class 1, as described in Table 6/1 compacted in compliance with Clause 612. Where mechanical compaction is impracticable, the backfilling shall be in ST2 concrete. The remainder of the backfilling shall be in appropriate capping and road pavement materials except that where mechanical compaction of capping or unbound mixture for subbase is impracticable ST2 concrete shall be used.

7 (mm/yy) Gully connection pipes shall be either flexible or rigid not exceeding 0.7 m in length with flexible joints for a distance of 2 m from the gully and shall be in accordance with Clause 507 when entering chambers. Junction pipes shall be manufactured of the same type and class of material as the remainder of the pipes in the run. Junction pipes which are laid but not immediately connected, shall be fitted with temporary stoppers or seals and the position of all such junctions shall be clearly defined by means of stakes or tracing wires properly marked or labelled. Saddles may be used to form junctions only where permitted in contract specific Appendix 5/1. No internal projections greater than 5 mm will be permitted. Saddles for plastics pipes shall be installed in accordance with the manufacturer's recommendations. Saddles with clay pipes shall be jointed with mortar designation (i) complying with Clause 2404, excluding lime. Saddles and pipes shall be surrounded with ST2 concrete.

8 (mm/yy) Where the adjustment or replacement of existing frames and gratings is required, the units shall be taken up and re-fixed or removed and replaced with new units complying with sub-Clauses 4 and 5 of this Clause, or as described in contract specific Appendix 5/1. On taking up or removal of the unit, any concrete or mortar bedding shall be broken out and the surface prepared. Where existing frames and covers or gratings are to be adjusted, the Contractor shall take up the unit and clean it so it is free from existing mortar, any debris, rust and is dry before re-use. The adjusted or replaced units shall be laid at a level, unless otherwise described in contract specific Appendix 5/1, 6 mm below the adjoining road surface on a mortar bed complying with sub-Clause 507.21. The finished thickness of the mortar bed shall be between 10 mm and 25 mm. Where required in contract specific Appendix 5/1, covers and gratings shall be bedded using a quick setting high strength mortar which shall have a declaration of performance for its intended use, the declaration of performance shall be provided to Overseeing Organisation before use. Any additional adjustment shall be made by modifying the brickwork in compliance with sub-Clause 507.3 or by using a frame of suitable depth. On completion of the works, each grating shall be lifted and the frame and seating cleaned.

509 Testing and Cleaning

1 Drains required in contract specific Appendix 5/1 to have watertight joints shall be tested as described in contract specific Appendix 1/5 in sections, eg. between chambers, by means of the air test described in sub-Clause 2 of this Clause. If a pipeline is rejected because of a failed air test, as part of the rectification work, a water test as described in sub- Clause 3 of this Clause may be carried out as an alternative compliance test. Before testing, the ends of the pipeline to be tested, including those of short branches, shall be plugged and sealed.

2 For the pipeline air test, air shall be pumped in by suitable means until a stable pressure of 100 mm head of water is indicated in a U-tube connected to the system. The air pressure shall not fall to less than 75 mm head of water during a period of 5 minutes without further pumping, after an initial period to allow stabilization. Drains with traps shall be tested to 50 mm head of water and the permissible loss shall then be no more than 13 mm head of water in 5 minutes without further pumping after the initial stabilising period.

3 For the pipeline water test, the pipes shall be filled with water under a head of not less than 1.2 m above the crown of the pipe at the high end and not more than 6 m above the pipe at the low end.

Steeply graded pipelines shall be tested in sections so that the above maximum is not exceeded. The test shall commence not less than two hours after filling the test section at which time the level of water at the vertical feed pipe shall be made up to produce the required 1.2 m minimum test head. The loss of water over a 30 minute period shall be measured by adding water at regular 10 minute intervals to restore the original water level and recording the amounts so added. The drain will have passed the test if the volume of water added does not exceed one litre per hour per linear metre of drain per metre of nominal internal diameter.

4 (mm/yy) All pipelines less than 350 mm diameter, excluding service ducts shall be checked by drawing through each completed length of pipe a spherical mandrel of a diameter 10% less than the nominal bore of the pipes being tested.

5 (mm/yy) During the progress of the Works all existing chambers, gullies and rodding eyes shall be kept clean and free from obstruction. On completion of the whole of the Works, all chambers, gullies and drains including verge/surface water drains and filter drains but excluding all fin and narrow filter drains shall be flushed from end to end with water and left free from obstructions and silt. Catchpit chambers shall be left clean and free from silt.

Unless otherwise required in contract specific Appendix 90/1 (MCHW 5.9.3) all carrier, foul and filter drains but excluding all fin and narrow filter drains shall be surveyed by Closed Circuit Television (CCTV) in accordance with the relevant requirements of Series 9000 (MCHW 5.9, Parts 1 to 5). Further guidance is provded in sub-Clauses NG 509.4 and NG 509.5.

6 The pipes and filter material of filter drains shall at all times be left clean and free from silt and obstruction.

7 Where described in contract specific Appendix 1/5, samples of one or more partly watertight joints for pipelines up to and including 900 mm diameter shall be tested with a head of water kept level with the crown of the pipe. The joint will not be accepted if the flow through the joint in litres per minute exceeds 20 times the square of the nominal internal diameter of the pipe in metres.

8 Permeability tests shall be as described in contract specific Appendix 5/1.

9 (mm/yy) Service ducts shall be checked by drawing a wooden mandrel, as shown on HCD Drawing Number I2, through as the ducts are laid. Where a set has to be given to the line of ducts the wooden mandrel shall be replaced by an iron mandrel 250 mm long but of the same diameter as the wooden version.

510 Surface Water Channels and Drainage Channel Blocks

1 Surface water channels and drainage channel blocks shall be constructed as described in contract specific Appendix 5/3.

2 Surface water channels shall comply with Clause 1103.

3 Drainage channel blocks shall comply with Clause 1101. Pre-cast concrete channel blocks shall comply with BS EN 1340. The declaration of performance shall be submitted to the Overseeing Organisation and it shall demonstrate that the channel blocks meet the specification.

511 Land Drains

1 (mm/yy) Existing land drains which are permanently severed by the Works shall be located and connected into a new drain, pipe or ditch all as described in contract specific Appendix 5/1. The lengths remaining within the Works shall be cleaned out from the new drain trench face as necessary. Any pipe disturbed by the Works shall be re-laid to ensure a free discharge into the new drain.

Disused ends of intercepted land drains shall be adequately sealed with ST2 concrete in compliance with Clause 2602.

2 Where an existing land drain is exposed and severed by temporary trench excavation, the Contractor shall mark the position of the drain and record it. The drain shall be diverted into an existing drain or watercourse. Alternatively, the normal functioning of the drain shall be continued by the construction of a pipeline or channel adequately supported across the excavation, until permanent restoration is made on the original line.

3 The Contractor shall notify the Overseeing Organisation of any land drain which is blocked or is otherwise defective when the drain is first exposed.

4 Severed mole drains shall be led straight into new drains; alternatively they shall where required in contract specific Appendix 5/1 be intercepted by the construction of a land drain. Where they have been disturbed mole channels shall be cleaned out and filled locally with Type A filter material or as otherwise described in contract specific Appendix 5/1.

512 Backfilling to Pipe Bays and Verges on Bridges

1 (mm/yy) Unless otherwise described in contract specific Appendix 5/1, filling to pipe bays and verges on bridges shall be well graded granular material not exceeding 20 mm size containing not more than 3% of material passing the 0.063 mm sieve and with a uniformity coefficient of more than 5. It shall be laid and compacted in compliance with sub-Clause 505.6 and 7. The material shall meet the sulfate requirement described in sub-Clauses 503.4, 503.5, 505.8 and 505.9.

513 Permeable Backing to Earth Retaining Structures

1 Unless otherwise described in contract specific Appendix 5/1, permeable backing shall consist of one of the following materials except when the filling adjacent to the structure is selected cohesive material (Class 7A), selected conditioned pulverised-fuel ash (Class 7B) or chalk:

- A minimum thickness of 300 mm of granular material complying with the requirements of Clause 505 for Type A or Type C material and, in addition, satisfying the following criteria:

  - Piping ratio (<5), defined as 15 per cent size of the drainage material, divided by 85 per cent size of the backfill material

  - Permeability ratio (>5), defined as 15 per cent size of the drainage material, divided by 15 per cent size of the backfill material where the per cent size of a material is the size of particle corresponding to the given per cent ordinate of the particle size distribution graph.

- Porous no-fines concrete, cast in situ 225 mm thick complying with the requirements of Clause 2603.

- (05/08) Precast hollow concrete blocks complying with the BS EN 771-3 laid in stretcher bond with dry joints in 225 mm thick walling with holes vertical. The blocks shall have a declaration of performance for their intended use which shall demonstrate that the blocks meet the specification.

2 (mm/yy) When the filling adjacent to the structure is selected cohesive material (Class 7A), selected conditioned pulverised-fuel ash (Class 7B) or chalk, the permeable backing shall be a minimum thickness of 300 mm of 0/4 or 0/2, CP or MP, sand complying with BS EN 12620 unless otherwise described in contract specific Appendix 5/1. The sand shall have a declaration of performance for its intended use which shall demonstrate that it meets the specification.

514 Fin Drains

General

1 Fin drains shall comply with this Clause and the special requirements described in contract specific Appendix 5/4.

The terms thickness, width, height and core shall have the meanings indicated on HCD Drawing Number F18 unless otherwise described in contract specific Appendix 5/4.

The term fin drain shall mean a planar geocomposite structure designed to perform the same function as a narrow filter drain.

2 Where fin drains are designed for lateral entry of water from one side only the requirements for flow rates in sub-Clauses 4 and 5 of this Clause shall apply to the face or plane designed to admit or transmit water.

3 The materials of which the drain is made shall be treated so that they are protected from the deleterious effects of short term exposure to ultraviolet light, and shall be resistant to degradation by acids, alkalis, common chemicals, bacteria, fungi and moulds occurring in soils and highway construction materials.

After exposure to ultraviolet light the Overseeing Organisation may require evidence that the materials still comply with the requirements of this Clause. The drain shall be protected from damage and ultraviolet light and be labelled to identify the grade and manufacturer or supplier. Where necessary, the side intended for entry of water and the direction of in-plane flow shall be identified.

Geotextile

15.7 4 The geotextile shall:

- conform to BS EN 13252 and the details stated in contract specific Appendix 5/4, it shall have a declaration of performance for its intended use, the declaration of performance shall demonstrate that the geotextile meets the specification and shall be submitted to the Overseeing Organisation prior to the commencement of fin drain work;

- (mm/yy) in both machine and cross-machine directions, sustain a tensile load of not less than 5.0 kN/m at break and have a minimum failure strain of 10% when determined in accordance with BS EN ISO 10319;

- (mm/yy) have a minimum static puncture resistance of 1200 N when determined in accordance with BS EN ISO 12236;

- (mm/yy) have a mean hole diameter < 40mm when tested to BS EN ISO 13433;

- have a size distribution of pore openings such that the apparent opening size O90 when determined in accordance with BS EN ISO 12956 is as stated in contract specific Appendix 5/4;

- have water permeability characteristics as stated in contract specific Appendix 5/4.

Composite Drain

(mm/yy) Where a composite drain is installed in an existing drain the following steps shall be undertaken:

- removal of approximately 400 mm depth of media from the drain.

- positioning of a non-woven geotextile over the exposed media.

- placement and compaction of sub-soil in compliance with Class 4 material (see Table 6/1) to form a V channel profile.

- placement of 35 mm to 50 mm of topsoil 15.9 (mm/yy) The maximum depth from the top of the topsoil to the channel invert shall be 200 mm.

(mm/yy) To ensure the grass roots get air as well as water after compaction, the subsoil shall be non cohesive and have a permeability in excess of 10-4 m/s as tested in accordance with HA 41.

5 (mm/yy) The composite drain shall:

- have a flow rate through each face of the drain of more than 75% of the value specified in sub-Clause 4(v) of this Clause on the side or sides where inflow occurs. This value may be found by either:

  - direct measurement of the composite drain using a modified version of BS 6906 : Part 3; or

  - calculation based on the flow rate obtained by the standard test in BS 6906 : Part 3 and the percentage contact area of the drainage core obtained from sub-Clause 13 of this Clause or other appropriate method;

- have values of long term in-plane flow rates as stated in contract specific Appendix 5/4 when determined in accordance with sub-Clauses 14 and 15 of this Clause. The values of hydraulic gradient and minimum applied stresses shall be as given in Table 5/7.

Table 5/7 (mm/yy) Applied Stresses (kN/m²) and Hydraulic Gradient

| HCD Drain Type | 5 | 6 | 7 | 10 |
| --- | --- | --- | --- | --- |
| Sub-Clause 14: Normal Stress Shear Stress | 50 10 | 50 10 | 50 10 | 50 10 |
| Sub-Clause 15: Normal Stress | 100 | 100 | 100 | 100 |
| Sub-Clause 15: Hydraulic Gradient | 0.1 1.0 | 1.0 | 1.0 | 0.1 1.0 |

Joints

6 Fin drains shall be capable of being jointed longitudinally or laterally into pipe systems or chambers for inflow and outflow purposes and be self jointing either directly or through purpose made attachment pieces for forming continuous drain lengths. All such joints shall be formed so as to prevent the ingress of soil particles or other extraneous material into the drain.

Fin drain joints transverse to the direction of flow shall have values of in-plane flow rates not less than that required by sub-Clause 5(ii) of this Clause.

Fin drain joints parallel to the direction of flow and any exposed edges shall be protected from the ingress of soil by a geotextile wrapping with a minimum overlap of 150 mm.

Pipes

7 (mm/yy) For drain Type 6 pipes shall be perforated or porous and comply with sub-Clause 501.3.

For drain Type 7 pipes shall be unperforated thermoplastics pipe complying with Clause 518 slotted longitudinally along the top surface and stress relief treated (if required) in accordance with the system manufacturer's specification.

8 (mm/yy) Pipe joints shall comply with the requirements of the relevant British Standard for the pipe used or Clause 518.

Backfill and Surround Material

9 Pipe surround material for drain Types 6 and 7 shall comply with sub-Clause 503.3(i) or 503.3(ii) or Type A or C material complying with sub-Clause 505.3.

Where fin drains are installed in a trench backfill material shall be the original as-dug material from the trench unless otherwise specified in contract specific Appendix 5/4.

Dimensions

10 (mm/yy) Unless otherwise described in contract specific Appendix 5/4 the dimensions of the fin drain shall be as shown on HCD Drawings F18 and F21. The pipe diameter shall be as stated in contract specific Appendix 5/4. The drain slope angle (x), as shown on Drawing F19, shall be not greater than 15% from the vertical unless otherwise stated in contract specific Appendix 5/4.

Installation and Handling

11 Installation of fin drains shall be as shown on HCD Drawing Numbers F19 to F21. Where fin drains are assembled on site the assembly area shall be clean and dry and free of wind-borne pollutants. Any material which becomes contaminated must be replaced. No geotextile or core material shall be exposed to daylight (or any source of ultraviolet radiation) for a period exceeding a cumulative total of 50 hours. Any geotextile or core material exposed to daylight (or any source of ultraviolet light) for a period exceeding a cumulative total of 50 hours shall be replaced unless it can be demonstrated that the materials of the drain still comply with the requirements of this Clause.

Where fin drains are laid in trench, the trench bottom shall be free of irregularities and to the required levels given in contract specific Appendix 5/4. Rock and other hard protuberances shall be removed and any excess cut in the trench bottom filled and compacted back to the required grade with suitable excavated or imported material.

The drain shall be laid with the appropriate face against the side of the trench adjacent to the carriageway and in the appropriate direction. This side of the trench shall have walls sufficiently clean to enable the fin drain to come into close contact with the wall when the trench is backfilled and compacted. Compaction shall be in accordance with Clause 612. Fin drains installed as part of the works shall be protected from surface water, contamination, and accidental damage during construction.

The fin drain, pipe surround and backfill shall be installed so as to cause no damage to the fin drain.

Where any damage does occur, the damaged materials shall be replaced by new material.

After the installation of the fin drain has been completed a marker tape shall be laid approximately 75 mm above the fin drain in the position shown on HCD Drawing Numbers F19 and F20. The tapes shall be green selfcoloured PVC or polythene plastic not less than 0.1 mm thick and 150 mm wide.

Identification

12 The Contractor shall obtain and make available the following information for each separate consignment of fin drain delivered to Site:

- geotextile declaration of performance;

- core name, grade/number and mass per unit area;

- names and addresses of system producer core and pipe manufacturers;

- manufacturing characteristics and constituents of core. This shall include composition and type of constituent filaments, threads, fibres, films, tapes and other components;

- consignment number and delivery date;

- a copy of the site delivery note.

Test Method for the Percentage Contact Area of Drainage Core

13 (i) The test determines the area of one face of a drainage core which will be in contact with a geotextile filter as a percentage.

(ii) The apparatus required is as follows:

- loading device able to apply a compressive load of at least 2 kN and having a flat steel base;

- flat steel loading plate 200 mm x 200 mm;

- printers ink and roller (or pad);

- sheet of thin compressible rubber;

- planimeter.

The test procedure shall be as follows. Cut three representative test specimens 200 mm x 200 mm (±2 mm). Apply ink to one 200 mm x 200 mm face of a specimen and cover with a sheet of plain paper and a thin compressible rubber sheet. Place the prepared specimen in to the loading device and gradually apply the load of 2 kN and maintain for 5 minutes. Release the load and remove the specimen and separate it from the paper. Using the planimeter find the total area of the paper which has received an imprint. Repeat for all specimens.

The percentage contact area = total area of imprint area of test specimen

The report shall include:

- a reference to this method;

- sample identification details;

- individual and mean percentage contact areas;

- details of any deviation from the specified test procedure.

Alternative methods of determining the percentage contact area may be employed with the prior approval of the Overseeing Organisation.

Test Method for Determining the Thickness of Fin Drains Under Specified Normal and Shear Stresses

14 (i) (mm/yy) The test determines the thickness of the fin drain under sustained normal and shear stresses. A long term thickness (at 100,000 hours) is calculated by extrapolation and a short term equivalent normal load which produces the long term thickness is determined.

(ii) The apparatus required is as follows:

- a suitable compression testing machine, which shall have a vertical travel at least the nominal thickness of the specimen. It shall be capable of sustaining the necessary loads to within 1% accuracy for the duration of the test;

- the compression testing apparatus, which shall include a fixed base plate and parallel moveable top plate with flat steel surface with sufficient friction to permit the development of the required shear forces;

- a means of measuring the mean thickness of the specimen to an accuracy of 0.01 mm.

As an alternative to (1) and (2), an appropriate inclined plane and kentledge system may be employed to produce the normal and shear loads.

The test procedure shall be as follows:

- Cut six representative specimens of minimum size 100 mm x 100 mm symmetrically about the core design. Three specimens shall be tested in accordance with (3) below and three in accordance with (4) below.

- The test specimen shall be placed symmetrically on the base plate and covered by the top plate. The means of measuring thickness shall be attached and the initial thickness measured.

- (mm/yy) Apply the load smoothly and as quickly as possible to the top plate. The full load (normal and shear) shall be applied in less than 20 seconds and sustained for at least 1000 hours. The applied stresses shall be those given in Table 5/7. At least four measurements of thickness shall be made during each unit of logarithmic time after the first minute. Determine the long term thickness of the specimen as the thickness of the specimen at 1000 hours reduced by 2T where T is the difference in thicknesses of the specimen thickness recorded at 100 hours and 1000 hours. Repeat the test on the two other specimens. The test specimens shall be maintained at a constant temperature of 20°C ± 2°C throughout the test period.

- Apply increasing increments of normal load to the specimen. Determine the short term equivalent load which shall be the load which when applied for a period of 20±5 minutes produces a specimen thickness equal (within an accuracy of ±0.05 mm) to the long term thickness of the specimen obtained at (3) above. Repeat the test on the other two specimens.

The report shall include:

- a reference to this method;

- sample identification details;

- the initial thickness of the sample;

- the applied load;

- the thickness of each sample at 100 and 1000 hours and the mean of the three results;

- a plot of percentage reduction in thickness against logarithmic time;

- the mean long term thickness;

- the mean short term equivalent load;

- any deviations from the specified test procedure.

Determining In-plane Flow Under Compressive Loading

15 (mm/yy) In-plane flow shall be determined in accordance with BS 6906 : Part 7 except that the following conditions shall apply: (a) the applied normal stress shall be the greater of the value given in Table 5/7 (for sub-Clause 15) or the mean short term equivalent stress as determined in sub-Clause 14 (vi) of this Clause; (b) the sample shall be tested such that the measured flow (or flows) is in the same direction as the principal flow (or flows) when the fin drain is in service; (c) the foam rubber option of the test procedure shall be used (details of the foam rubber to be used may be obtained from the Overseeing Organisation); (d) the hydraulic transmissivity shall be reported for each of the hydraulic gradients employed.

Test Methods

16 Notwithstanding the requirements of sub-Clauses 13, 14 and 15 of this Clause, variations in the test methods specified therein shall be made where deemed necessary by the British Board of Agrément following consultation with the manufacturer. All such variations shall be recorded in the report.

Certification

17 Fin drains and constituent materials, other than the geotextile and aggregates, shall have current product acceptance scheme certification in accordance with sub-Clauses 104.15 and 104.16 certifying the appropriate physical properties when tested in accordance with this Clause.

515 Narrow Filter Drains

General

1 Narrow filter drains shall comply with this Clause and the special requirements described in contract specific Appendix 5/4.

The term narrow filter drain refers to drain Types 8 or 9 indicated in the HCD Drawing Number F18.

They consist of a porous or perforated pipe laid in a narrow trench surrounded by granular material where the granular material and/or the pipe is enclosed by a layer of geotextile filter. Narrow filter drains and fin drains perform the same function.

Materials

2 The materials used in the drain shall be stored so that they are protected from the deleterious effects of short term exposure to ultraviolet light, and shall be resistant to degradation by acids, alkalis, common chemicals, bacteria, fungi and moulds occurring in soils and highway construction materials.

After exposure to ultraviolet light the Overseeing Organisation may require evidence that the materials still comply with the requirements of this Clause. They shall be protected from damage and ultraviolet light and be labelled to identify the grade and manufacturer or supplier.

3 The geotextile used in narrow filter drains shall comply with all requirements of sub-Clause 514.4 for geotextiles used in fin drains.

For drain Type 8 the geotextile surround to the pipe shall consist of a prefabricated continuous close fitting sock. Alternatively the pipe shall be firmly wrapped in a single layer of geotextile with an overlap of between 50 and 75 mm and secured around the pipe in a manner so as to prevent the ingress of soil particles or other extraneous material and without affecting the permeability of the wrapped material.

Splices between lengths of sock or layer shall have overlaps within these dimensions and be securely tied.

For drain Type 9 the geotextile surround to the granular material shall have a minimum overlap of 250 mm including 100 mm down-tuck. Splicing of lengths of geotextile shall consist of minimum 600 mm overlap secured with pins or mechanical ties. Where an outlet pipe passes through the geotextile a separate piece of geotextile shall be wrapped round the outlet pipe, flared against the geotextile in the filter drain and secured.

Where drain lengths are terminated at chambers, the geotextile shall be secured against the chamber walls by suitable means so as to prevent the ingress of soil particles or other extraneous material into the drain.

4 (mm/yy) Pipes and fittings shall comply with sub- Clauses 514.7 and 514.8. Where coilable pipes are used they shall be capable of being straightened so as to lie flat without restraint in the trench bottom before backfilling.

5 (mm/yy) The granular material used for trench infill shall comply with the requirements for non-plasticity, LA category and sulfate content of sub-Clause 505.7 and have a grading within the limits of Table 5/8. The material shall meet the permeability requirements described in contract specific Appendix 5/4.

Table 5/8 Narrow Filter Drain: Trench Infill Grading Requirements

|  | Type 8 | Type 9 |
| --- | --- | --- |
| Standard | BS EN 13242 | BS EN 13242 |
| Size, mm | 1/20 | 10/40 |
| Grading | GC 80-20 | GC 85-15 |
| Aggregate | Coarse | Coarse |
| Category for tolerances at mid-size sieves | as stated in contract specific Appendix 5/4 | as stated in contract specific Appendix 5/4 |
| Category for maximum fines | f2 | f2 |
| Additional requirements | d/8 | d/80 |
|  | 0-3% passing by mass | 0-3% passing by mass |

Dimensions

6 Unless otherwise described in contract specific Appendix 5/4 the dimensions of the narrow filter drain shall be as shown on HCD Drawing No. F18. The pipe diameter shall be as stated in contract specific Appendix 5/4. The drain slope angle (x), as shown on Drawing F20, shall be not greater than 15% from the vertical unless otherwise stated in contract specific Appendix 5/4.

Installation and Handling

7 Narrow filter drains shall be installed as shown on HCD Drawing Number F20. Before during and after installation the geotextile shall be protected from contamination, damage and exposure to ultraviolet radiation in accordance with sub-Clause 514.11.

The excavated trench bottom shall be free of irregularities and to the required levels given in contract specific Appendix 5/4. Rock and other hard protuberances shall be removed and any excess cut in the trench bottom filled and compacted back to the required grade with suitable excavated or imported material. Drain Type 9 shall have trench walls sufficiently clean to enable the geotextile to come into close contact with the wall when the granular material is placed inside it. The deposition and compaction of infill shall be in accordance with sub-Clause 505.4 for filter drains.

Narrow filter drains installed as part of the works shall not be used for the disposal of surface water run-off during construction. Narrow filter drains exposed to surface water ingress shall be temporarily protected.

Marker tapes shall conform and be installed in accordance with sub-Clause 514.11.

8 The Contractor shall obtain and make available the information required in sub-Clause 514.12 in respect of the geotextile and pipe.

516 Combined Drainage and Kerb Systems

(mm/yy) General

1 (mm/yy) Combined drainage and kerb systems listed in contract specific Appendix 1/10 shall be treated as features to be designed by the Contractor. Combined drainage and kerb systems shall conform to BS EN 1433 and to the special requirements in contract specific Appendix 5/5.

2 (mm/yy) Combined drainage and kerb systems shall be suitable for their intended use and place of installation in the works and as stated in contract specific Appendix 5/1.

The Contractor shall provide a declaration of performance for each type of combined drainage and kerb system proposed to the Overseeing Organisation prior to the commencement of drainage works. The declaration(s) of performance shall demonstrate that the system(s) meet the requirements of the specification.

3 (mm/yy) Design flows given in contract specific Appendix 5/5 shall be accommodated without surcharge within the main combined drainage and kerb section and beneath the underside of any inlet slot sections.

4 (mm/yy) Where applicable, the width and depth of combined drainage and kerb system units shall not exceed the dimensions given in contract specific Appendix 5/5.

5 (mm/yy) When used adjacent to pervious surfacing materials, units shall incorporate side entry inlets to permit drainage of water held within the pervious surfacing. Inlets shall comply with the requirements of contract specific Appendix 5/5 and shall have the capacity to drain pervious surfacing.

(mm/yy) Classification

6 (mm/yy) Combined drainage and kerb systems, excluding in-situ system, shall be classified as follows according to their intended use and shall be as stated in contract specific Appendix 5/5:

- C 250:

- D 400; and

- where, exceptionally, combined kerb and drainage units have to be located in areas subjected to large numbers of high speed heavy goods vehicles, Class E600 combined kerb and drainage units shall be considered.

(mm/yy) Water Tightness

7 (mm/yy) Joints between units comprising the system and between the channel and units, shall be designed to avoid leakage of surface water. Joints between bridge deck waterproofing and component parts passing through the waterproofing shall be watertight. Sealants shall be compatible with the waterproofing system.

(mm/yy) Installation and Handling

8 (mm/yy) Combined drainage and kerb systems shall be laid and jointed in accordance with the manufacturer's instructions.

9 (mm/yy) Adjacent carriageway, footway, verge or central reserve to bedding, backing, surrounding or jointing of combined drainage and kerb units shall be in accordance with the manufacturer's instructions.

10 (mm/yy) Junctions, connecting pipes and other fittings comprising the combined drainage and kerb system shall comply with sub-Clause 501.3 and shall be as described in contract specific Appendix 5/5.

The combined drainage and kerb system shall incorporate measures to enable rodding of the outfall pipework and adequate access for jetting by water jetting equipment into the system.

(mm/yy) Cleaning

11 (mm/yy) Combined drainage and kerb systems shall be cleaned out by appropriate means and shall be left clean and free from all obstruction. The completed combined drainage and kerb systems shall be surveyed in accordance with the relevant requirements in contract specific Appendix 5/5.

517 Linear Drainage Channel Systems

General

1 (mm/yy) The linear drainage channel systems listed in contract specific Appendix 1/10 shall be treated as features to be designed by the Contractor and shall conform with requirements stated in contract specific Appendices 1/10 and 5/6. In-situ linear drainage channel systems shall conform, where applicable, to sub-Clauses 517.2 to 517.17. Prefabricated, or manufactured, linear drainage channel systems shall conform to BS EN 1433.

2 (mm/yy) Linear drainage channel systems shall be suitable for their intended use and place of installation in the works. The Contractor shall provide evidence of such suitability for the purpose to the Overseeing Organisation. For prefabricated or manufactured linear drainage systems this shall be the declaration of performance. The declaration of performance shall demonstrate that the linear drainage system meets the requirements of the specification.

3 Design flows given in contract specific Appendix 5/6 shall be accommodated without surcharge within the main channel section and beneath the underside of any inlet slot sections.

4 (mm/yy) Where applicable, the width and depth of linear drainage channel system units shall not exceed the dimensions given in contract specific Appendix 5/6.

5 (mm/yy) Dimensions of inlet slots shall comply with the following criteria:

- for prefabricated linear drainage channel systems they shall conform to BS EN 1433;

- for in-situ linear drainage channel systems they shall conform to BS EN 1433.

6 (mm/yy) When used adjacent to porous asphalt surfacing materials, units shall also incorporate side entry inlets to permit drainage of water held within the porous asphalt. Inlets shall comply with the requirements of contract specific Appendix 5/6 and shall have the capacity to drain porous asphalt.

(mm/yy) Weathering Resistance

7 (mm/yy) Marking relating to the grade of weathering resistance for drainage channels made of concrete shall be as stated in contract specific Appendix 5/6.

(mm/yy) Classification

8 (mm/yy) linear drainage channel systems shall be classified as follows according to their intended use and shall be as stated in contract specific Appendix 5/6:

- C 250;

- D 400; and

- where, exceptionally, linear drainage channel systems have to be located in areas subjected to large numbers of high speed heavy goods vehicles, Class E600 combined kerb and drainage units shall be considered.

(mm/yy) Water Tightness

9 (mm/yy) Joints between units comprising the system and between adjacent construction and the system shall be designed to avoid leakage of surface water. Where applicable, joints between bridge deck waterproofing and component parts passing through the waterproofing shall be watertight.

Sealants shall also be compatible with the waterproofing system.

10 (mm/yy) Junctions, connecting pipes and other fittings comprising the linear drainage channel system shall comply with sub-Clause 501.3 and shall be as described in contract specific Appendix 5/6. The linear drainage channel system shall incorporate measures to enable rodding of the outfall pipework and adequate access for jetting by water jetting equipment into the system.

(mm/yy) Cleaning

11 (mm/yy) The linear drainage channel systems shall be cleaned out by appropriate means and shall be left clean and free from all obstruction on completion of the works. The completed linear drainage channel systems shall be surveyed in accordance with requirements stated in contract specific Appendix 5/6.

In Situ Systems

12 (mm/yy) In-situ systems shall comply with the requirements of sub-Clauses 1103.1, 1103.3 and 1103.4.

They shall also comply with the requirements of sub-Clause 1103.2 except that the concrete shall be considered as plain concrete within the terms of this sub-Clause, irrespective of the inclusion of reinforcement.

13 (mm/yy) In-situ systems shall be slip formed except for sections at gullies which shall be hand formed. Full depth joints shall be constructed at the interface at each side of gullies with a 25 mm thick filler board complying with Clause 1015 and sealed in accordance with Clauses 1016 and 1017.

14 (mm/yy) The central void may be formed by an inflated tube which is then removed, or by an in situ suitable pipe or similar former fit for the purpose. At gully positions the inner former shall be pre-sleeved with a suitable pipe or similar former fit for the purpose which shall be of sufficient length to overlap the two joints on either side of the gully.

15 (mm/yy) The central void shall be checked in accordance with sub-Clause 509.4. Verification of slot widths shall be determined by suitable templates.

16 (mm/yy) Reinforcement shall comply with Series 1700. Cover to reinforcement shall be not less than 75 mm.

17 (mm/yy) Trial lengths and testing of in-situ channels shall be undertaken in accordance with contract specific Appendix 1/5 and clauses 6 and 8.6 of BS 5931 and the relevant paragraphs of clause 9 of BS EN 1433 respectively.

518 (mm/yy) Thermoplastics Structured Wall Pipes and Fittings

General

1 Thermoplastics structured wall pipe shall comply with this Clause and the special requirements described in contract specific Appendix 5/1.

The term structured wall pipe shall mean all types of smooth bore pipe except solid wall homogeneous pipe.

Typical forms of construction classified as structured wall pipes include: single wall externally structured smooth bore, twin wall, foamed core and spirally wound.

The term fitting shall mean a product used in conjunction with the pipe to form the system but excluding gullies manhole chambers, inspection chambers and access chambers.

Materials

2 The materials from which the pipe and fittings are made, shall be treated so that they are protected from the deleterious effects of short term exposure to ultraviolet light, and shall be resistant to degradation by acids, alkalis, common chemicals, bacteria, fungi and moulds occurring in soil, highway construction materials and highway drainage systems. In addition, the materials from which the pipe and fittings are made, shall not incorporate any additives in quantities sufficient to cause microbiological degradation or to impair the conformity to the chemical, physical and mechanical properties or impact resistance requirements given in sub-Clause 5 of this Clause. The specification of the raw material shall be agreed between the certification body, as defined in sub-Clause 15 of this Clause, and the manufacturer and may incorporate re-processable and/or recyclable material. The agreed specification shall incorporate tolerances for each of the relevant characteristics defined in the appropriate clause of BS EN 13476. The Contractor shall submit to the Overseeing Organisation, prior to commencement of the works, completed information sheets in accordance with contract specific Appendix 5/7.

Dimensions

3 Systems for carrier drainage shall be between 150 mm and 900 mm nominal internal diameter. Pipes for narrow filter drains shall be 110 mm or 150 mm nominal internal diameter. Pipes for service ducts shall have nominal internal diameters of between 50 mm and 150 mm. Pipes for sub-soil drainage shall incorporate slots or holes with a minimum cross sectional area of 1000 mm2 per metre run of pipe.

The bore of the pipe and fittings shall be in accordance with the standard tolerances for nominal bores given in BS EN 476.

Appearance

4 (mm/yy) The system shall have a smooth bore and be free from any burs, flash or other inconsistencies that could have a detrimental effect on the performance of the system. Pipes and fittings for drainage shall be externally coloured either terracotta or black. The colour of ducting pipes shall be in accordance with National Joint Utilities Group publication "Guidelines on the Positioning and Colour Coding of Utilities' Apparatus".

Any variation in the colour shall be described in contract specific Appendix 5/2.

Structured Wall Pipe

5 The structured wall pipe shall have the properties defined in Table 5/9.

Table 5/9 Requirements for Structured Wall Pipe

| Property | Relevant Standard | Requirement |
| --- | --- | --- |
| General | BS EN ISO 2897-1,BS EN ISO 2897-2 and BS ISO 11922-1 | Dimensions to be specified |
| Ring stiffness | BS EN ISO 9969 6 | kN/m2 minimum. Lower stiffness values are permitted if design calculations to BS EN 129 5-1 (UK national annex), based on site specific installation conditions, indicate satisfactory performance.) |
| Creep Ratio | BS EN ISO 9967 | PVC-U - maximum 2.5 PP and PE - maximum 4.0 |
| High volume low pressure jetting | WRc Jetting Test Method | Minimum acceptable failure pressure 137 bar. |
| Longitudinal bending | sub-Clause 518.11 | Pipes with nominal diameters ≤ 350 mm to have a difference in dimensions when measured in the vertical axis of less than 5% of the pipe length and no local permanent deformation occurs during the test. |
| Impact resistance at 0 ºC | BS EN 1411 with d25 striker of 1 kg | Preliminary test – test 10 pieces as described in BS EN 1411, dropping the striker from a height of 1m. If any test pieces fail, subject the pipe to the full test given in clause 7.3 of BS EN 1411 starting the striker from a drop height of 400 mm. The mean minus1.64 times the standard deviation must exceed 1m. |
| Impact resistance at 2 3ºC | BS EN 1411 with striker as above | Value to be derived from the same batch of pipe as used in the impact resistance test at 0ºC. The H50 (mean) value - 10% to be used as the minimum value for quality control testing. Alternatively the 0°C test can be used as a QC test if the manufacturer chooses. |
| Rodding resistance | sub-Clause 518.12 | Pipes with nominal diameters ≤ 350 mm to have an average failure energy >3 joules |
| Static friction coefficient (ducts) | TS 12-24 | Pass |
| Creep at elevated temperature (ducts) | BS EN ISO 9967 | Test to be carried out at 45ºC, creep ratio to be less than 2 times the values to BS EN ISO 9967. |
| Resistance to point loads (ducts) | sub-Clause 518.13 | No perforation at 10% rod travel Tensile strength of a seam BS EN 1979 prEN 13476 |

Fittings

6 The fittings for use with structured wall pipe shall have the properties defined in Table 5/10.

Table 5/10 Requirements for Fittings

| Property | Relevant Standard | Requirement |
| --- | --- | --- |
| General | BS EN ISO 2897-1, BS EN ISO 2897-2 and BS EN ISO 11922-1 | Dimensions to be specified |
| Ring stiffness (excluding couplers) | BS EN ISO 13967 | 6 kN/m2 minimum |
| Rodding resistance | sub-Clause 518.12 | Fittings with nominal diameters ≤ 350 mm to have an average failure energy >3 joules |
| Strength and flexibility of fabricated fittings | BS EN 12256 | BS EN 12256 |
| Impact resistance (drop test) | Drop Test to BS EN 1 2061: 1999 | Fall height 1000 mm at a temperature of 0ºC. Product less than ND 300 shall show 'no damage'. Others may fail but must be identified as 'handle with care' |
| Watertightness of fabricated fittings | BS EN 1053 | 0.5 bar for 1 minute |

Pipe and Fittings

7 The pipe and fittings shall have the properties defined in Table 5/11.

Table 5/11 Requirements of the Systems

| Property | Relevant Standard | Requirement |
| --- | --- | --- |
| Leaktightness of joints - diameter distortion (watertight joints) | BS EN 1277 Method 4 condition B Temperature (23 ± 2)°C | Use default values from BS EN 127 7 |
| Leaktightness of joints - angular deflection (watertight joints) | BS EN 1277 Method 4 Condition C Temperature (23 ± 2)°C | Use default values from BS EN 127 7 |
| Leakage rate from partially-watertight joints | sub-Clause 509.7 | Less than 20 times the square of the ID of the pipe in metres shall flow through the joint in litres per minute |
| Resistance to wheel loads | BS EN 1437 adapted to suit HA loading conditions | Less than 5% deformation when loaded to 100 kN (for unequal branches only) |

Bedding, Backfill and Surround Material

8 (mm/yy) All systems shall be installed in accordance with the pipe and bedding combinations given in Advice Note HA 40 (DMRB 4.2.5). Other combinations shall be supported by calculations in accordance with BS EN 1295-1 UK National Annex. Bedding, backfill and surround materials are classified in Clause 503 and Clause 505.

Installation and Handling

9 The bedding, surround and backfill shall be installed so as to cause no damage to the pipes and fittings. Installation of the pipe and fittings, particularly, procedures for preparation and execution of jointing operations, shall be in accordance with the manufacturer's instructions.

Identification

10 The Contractor shall maintain records with the following information for each separate consignment of structured wall pipe or fittings delivered to Site:

1) system name, ring stiffness grade/number and size;

2) name and address of the system manufacturer;

3) consignment number and delivery date; and 4) a copy of the site delivery note.

Test Method for Longitudinal Bending

11 The test specimen shall be a six metre length of pipe or the maximum length available from the manufacturer (if less than six metres).

The apparatus shall include:

1) two level support blocks at least 250 mm wide and of sufficient height to allow the pipe to sag over its length without touching the ground;

2) a means of measuring the vertical distance between the pipe at the centre of the span and a fixed point of reference to an accuracy of ±0.5 mm.

The test procedure shall be as follows:

1) condition the specimen for at least 1 hour at 23°C ± 2°C;

2) set the supports at a distance apart equal to the length of pipe minus 500 mm;

3) place the pipe symmetrically on the supports;

4) measure the distance between the top of the supports and the fixed point of reference, in the vertical axis through the centre line of the pipe;

5) after a period of two minutes measure the distance between the underside of the pipe at mid span and the fixed point of reference;

6) record the difference in readings as a percentage of pipe length.

Test Method for Rodding Resistance (Internal Puncture)

12 The test specimens shall be:

1) twenty specimens cut from the structured wall pipe, each specimen to be 242 mm to 246 mm in length and a quarter section of the circumference or;

2) twenty specimens cut from a number of identical fittings.

The apparatus shall include:

1) a standard drop weight pipe testing apparatus capable of dropping a tup from a height of 1 m;

2) a 300g tup which can be varied in 30g multiples with a striker consisting a steel rod 18 mm in diameter with a 9 mm hemispherical end;

3) a 250 mm x 250 mm box containing dry Leighton Buzzard sand (Garside quarry) such that there is at least 100 mm of sand beneath the test specimen when bedded down.

Procedure shall be as follows:

1) mark the intended point on the inside of the pipe on the intersection of the centre lines. With profiled pipes the point of impact shall be at the point nearest the intersection that mid way between the ribs or in the middle of a hollow corrugation;

2) alternatively mark the intended point of impact on the section of fitting;

3) condition the test specimens in air at a temperature of 4°C ± 2°C for a period of at least one hour before the test;

4) locate the box under the drop tube of the impact apparatus;

5) embed the specimen into the sand using a vibrator with the inner surface exposed and facing upwards;

6) locate the specimen such that the marked point of impact is under the centre line of the tup;

7) drop the tup from a height of 1 m on to the inner surface of the specimen within 10 seconds of removing the specimen from the conditioning environment;

8) examine the specimen for damage.

NOTE Damage is defined as a puncture or crack of the inner layer. Ductile bending or "whitening" is not considered to be damage;

(mm/yy) if the specimen exhibits no damage the next test shall be conducted with a tup of 30 g greater mass. If the specimen does exhibit damage the next test shall be conducted using a tup of 30 g smaller mass;

After having completed the 20 strikes calculate the average of the energies where a pass (no damage) was recorded and the average of the energies where a failure (damage) was recorded, then calculate the average of the two averages.

The test report shall include:

1) identification of the samples;

2) the overall average;

3) whether or not the specimens were damaged.

Test Method for Resistance to Sharp Objects

13 Test specimens shall be three samples of duct each 300 mm long.

The apparatus shall include:

1) a compression testing machine;

2) a 4.7 mm diameter steel rod with an hemispherical end;

3) and a 120° steel vee block at least 300 mm long.

The test method shall be as follows:

1) condition the test specimens for at least 1 hour at 23°C ± 2°C;

2) insert the steel rod in the jaws of the moveable platen of the compression testing machine so that the hemispherical end protrudes at least 15% of the nominal pipe diameter;

3) (mm/yy) position the specimen in the vee block and place directly below the steel rod, for twin-walled pipe the specimen shall be positioned firstly so that the rod strikes on the corrugation or rib, and secondly in the valley (where possible);

4) set the machine to lower at a rate of 5 mm/min;

5) allow the rod to travel into the pipe a distance equal to 10% of the nominal internal diameter of the pipe (T10 mm) or until the pipe wall is perforated. When the outer skin of a twin wall pipe is perforated before 10% is attained, the rod travel up to the point of failure shall be recorded (Tf mm) and the rod allowed to travel to the inner wall. The rod travel shall be continued to a total of 10% (i.e.T10 - Tf) or until complete penetration occurs.

6) For each test specimen: pipe size, reference, maximum load and rod travel shall be recorded.

Notwithstanding the requirements of sub-Clauses 11, 12 and 13 of this Clause, variations in the test methods specified therein shall be made where deemed necessary by the British Board of Agrément (or equivalent) following consultation with the manufacturer and in agreement with the Overseeing Organisation. All such variations shall be recorded in the report.

Certification

15 Pipes and fittings shall have current product acceptance scheme certification in accordance with sub-Clauses 104.15 and 104.16 certifying the appropriate physical properties when tested in accordance with this Clause.

519 (mm/yy) Concrete Bagwork

1 (mm/yy) ST4 concrete in compliance with Clause 2602 shall be used throughout. The concrete filling to the bags shall have a low workability with a slump of 25 mm.

2 The bags shall be hessian sand bags complying with BS 1214. The size of the bags shall be such that when filled, the dimensions shall be 450 mm x 300 mm x 150 mm. The bags shall be placed in position and shaped to the profile shown on the drawings by striking with a flat timber board until all faces are flat and all edges square.

3 The finished exposed faces of the bagwork shall not be punctured or torn and no tucked ends shall be visible.

4 Each concrete bag is to be spiked to the one below and the bottom row spiked to the foundation with 10 mm x 200 mm mild steel dowel bars. Where the concrete bags have a concrete backing, alternate rows of bags shall be spiked to the backing concrete with 10 mm x 200 mm mild steel dowel bars at 45 degrees to the horizontal with one dowel per bag in the row.

5 (mm/yy) Where bagwork forms a headwall, headwall foundations are to be cast against the excavated face and any overdig filled with ST4 concrete.

6 Formed concrete surfaces shall be to Class F1 finish and unformed surfaces to Class U1 finish in accordance with Clause 1708.

7 Where bagwork is provided to protect watercourses, before placing the bags, the banks shall be cut into horizontal steps to provide a suitable foundation and shall be covered in geotextile to the requirements of Clause 609. The bottom course of bags shall be at least 450 mm below the stream bed and all succeeding courses shall be horizontal and all vertical joints shall be staggered in alternate courses. Headers shall be placed at every third bag in alternate courses.

8 The bagwork shall be thoroughly soaked with water upon completion of the construction to saturate the hessian bags.

520 (mm/yy) The Cleaning of Existing Drainage Systems

1 Where stated in contract specific Appendix 5/1, the Contractor shall clean existing drainage systems in accordance with this Clause.

2 2 The Contractor shall take measures when clearing blocked drains to ensure that adjacent water courses or groundwater via soakaways, will not be contaminated.

Contamination includes mud or soil being washed or flushed into streams as well as other more obvious contaminants including diesel fuel, oil and chemicals.

3 (mm/yy) Initial attempts to clear blocked drains prior to jetting, shall be undertaken by hand rodding and any debris and silt removed by the operation shall be removed off site. The Contractor shall report any localised blockages that cannot be cleared by rodding to the Overseeing Organisation.

4 (mm/yy) Where jetting is required in contract specific Appendix 5/1 the procedures stated in Clause 521 shall be followed.

Cleaning of Gullies, Catchpits, Soakaways and Oil Separators

5 At each chamber all mud and vegetation in the vicinity of the chamber likely to impede the flow of water shall be removed. After lifting the cover or grating the chamber shall be cleansed of all water, detritus, debris and silt, refilled with clean water to the outlet level, and all covers and gratings replaced and evenly bedded.

6 (mm/yy) Cleaning of chambers shall be by mechanical means. The vehicle used to clean existing chambers shall be equipped with a 125 mm dia gulley arm with boom jets, an exhauster with a minimum output of 5.95 cum/min and minimum 5455 litres capacity. Sediment, detritus and liquor from the chamber shall not be permitted to discharge into the outlet. This may be achieved either by plugging the outlet during cleaning, or by simultaneous jetting and abstraction of liquor from the chamber using a tanker fitted with low pressure high volume water jets around the boom.

7 Gullies and chambers not cleaned for whatever reason, blocked connections and broken or cracked covers, gratings or frames shall be marked to aid subsequent identification.

8 Oil separators shall be refilled with uncontaminated water following the cleaning operation.

9 (mm/yy) The Contractor shall dispose of all surplus water, debris and arisings from the works off site at a licensed tip.

Cleaning or Testing of Piped Drainage Systems and Subway Drainage Channels

10 (mm/yy) Routine cleaning or testing of piped drainage systems and subway drainage channels shall be carried out by rodding or low pressure high volume jetting in accordance with Clause 521.

11 (mm/yy) The location of any obstruction that cannot be removed by flushing shall be marked on the ground using a wooden peg or other semi-permanent means and reported to the Overseeing Organisation using the Routine Maintenance Manual System (RMMS) referencing system in Part 3, Chapter 3.7.

12 All covers which have been removed for cleaning operations shall be replaced and evenly bedded.

13 The Contractor shall report any damage and defects to the drainage system or components to the Overseeing Organisation each day, or immediately if considered a safety hazard.

Cleaning Kerb or Channel Offlet Pipes

14 Where necessary all vegetation and debris shall be removed from around metal kerb weirs and the cover lifted for cleaning.

15 Offlets shall be cleaned such that all silt and loose obstructions are removed from the pipe. This shall be achieved by rodding or by using lorry-mounted drain clearance equipment comprising combination pressure jetting with high air flow suction equipment. The vehicle shall also be equipped with a hydraulically powered grid lifter.

16 The Contractor shall ensure that each end of the offlet is free from vegetation or other obstructions including any material expelled from the pipe. Where the invert of the outlet is below the invert of the ditch, the bottom of the ditch shall be excavated until the invert of the pipe is exposed and the ditch invert regraded to facilitate flow from the outlet.

17 The location of any obstruction that cannot be removed shall be marked on the ground using a wooden peg or other semi-permanent means and reported to the Overseeing Organisation.

18 All covers lifted for cleaning operations shall be replaced and evenly bedded.

Cleaning of Bridge Drainage Systems

19 Cleaning of bridge bearing shelves, subway sumps, grit chambers and other bridge drainage systems shall be carried out by one of the following methods:

1) vacuum/air suction having the ability to remove materials from depths of up to 9.0 m with a suction facility capable of displacing 55 m3/min of air at 95% vacuum;

2) (mm/yy) low pressure high volume jetting in accordance with Clause 521;

3) sweeping.

20 All adjacent surfaces of the structure shall be protected to prevent staining by arisings from the cleaning operation. All arisings shall be taken off site.

21 The Contractor shall report to the Overseeing Organisation any damage or defects to the bridge drainage system.

521 (mm/yy) Low Pressure High Volume Jetting of Drainage Systems

1 Where stated in contract specific Appendix 5/1, the Contractor shall clean existing drainage systems in accordance with this Clause.

2 The drainage systems to be cleaned shall be as detailed in the contract specific Appendix 5/1.

The pipe material of the drainage systems to be cleaned shall be identified in contract specific Appendix 5/1. Where the material is unknown and cannot be verified by either visual inspection, without recourse to man-entry, or from drainage records, or damage to the pipeline is the suspected cause of a blockage, cleaning shall proceed on the basis of use of the lowest pump pressure stated in Table 5/12.

4 Where the cleaning forms part of the pre-cleansing works for the CCTV survey of drainage systems, the works shall be detailed in contract specific Appendix 90/1 (see Model Contract Documents for CCTV Survey of Highway Drainage, (MCHW 5.9.3).

Jetting of Piped Drainage Systems

5 Cleaning shall take place from downstream of the blockage in an upstream direction. The pipe shall be plugged below the jetting point to prevent contaminants flowing to the watercourse. The cleaning shall take place from a chamber, although it may be necessary to make a temporary excavation into the pipeline in some circumstances.

6 Should the Contractor find that it is not possible to jet in an upstream direction, then the pipe shall be plugged below the blockage and the jetter then used to "back jet" to a suction hose.

Table 5/12 Maximum Recommended Pump Pressures

| Material | Maximum pump pressure (bar/psi) |
| --- | --- |
| Unknown/structurally damaged | 80/1200 |
| Brick/masonry | 100/1500 |
| Plastics - Structural Wall | 127/1900 |
| Plastics - Solid Wall | 127/1900 |
| Concrete | 340/5000 |
| Clay | 340/5000 |

7 The Contractor shall select a jethead that is appropriate for delivering the maximum jetting pressure for the pipe material and also the minimum volume of water for the appropriate pipe diameter stated in Table 5/13.

8 The jet head shall be of a configuration such that the number and direction of jets are adequate to be directed to the sides and soffit of the pipeline to prevent debris passing over the top of the jetting head.

Table 5/13 Minimum Jetting Flow Rates

| Pipe Diameter | Minimum jetting flows |
| --- | --- |
| <230 mm | 156 l/m |
| 450 mm | 270 l/m |
| 900 mm | 300 l/m |
| 1600 mm | 342 l/m |

9 The Contractor shall provide suitable jetting equipment that shall include the provision of the following:

1) operation at a maximum rate of 850 l/min at 150 bar/2250 psi;

2) liquid ring vacuum pump operating with air flows of 4000 m3 per hour, with a working vacuum of not less than 90%;

3) a minimum of 20 m of 100 mm diameter suction hose for cleaning pipes up to 300 mm diameter and 150 mm diameter suction hose for cleaning pipes of diameter greater than 300 mm;

4) minimum of 150 m of 25 mm or 38 mm diameter jetting hose and a capability of jetting up to 200 m;

5) automatic and continuous water recycling;

6) silt, sand and rubble to be de-watered prior to discharge at licensed tip.

10 The Contractor shall ensure that no damage occurs to the manhole chamber or pipeline during insertion of the jetting equipment.

11 (mm/yy) The jetting head shall be propelled through or over the blockage and then the hose pulled backwards enabling the force of the jet to break up the blockage material. The minimum force necessary to penetrate the blockage shall be used but the pump pressures should not exceed those stated in Table 5/12.

12 The hose shall be rewound at a rate of between 100 mm and 200 mm per second.

13 There is a possibility that damage may occur to certain pipe materials should the jetting head remain stationary thus the Contractor must ensure that the jetting head never remains stationary for more than 60 seconds.

14 Where the presence of perforated pipes and porous concrete pipes in piped highway drainage systems is discovered during the course of the works, the Overseeing Organisation shall be notified immediately and the cleaning operation suspended for that section of the works.

Cleaning of Linear Drainage Systems

15 Where possible the Contractor shall clear blockages in linear drainage channels and combined kerb drainage units by rodding.

16 Where silt removal is necessitated, the use of pressure jetting will result in the loss of pressure through the grating, slot or drainage holes together with the escape of silt and debris, unless the apertures can be temporarily covered. The application of pressure shall be regulated such that there is only sufficient to drive the jetting head across the silt to access remote from the point of entry.

17 If necessary the jetting head shall be changed for one that can deliver the highest volume of water at low pressure. The water pressure shall be sufficient to agitate the silt.

18 The nozzle shall be drawn back to the point of entry at a rate of between 100 mm and 200 mm per second.

Silt Removal

19 Suitable measures such as stanks or stoppers shall be positioned downstream of the drainage system to be cleaned to minimise the risk of sediment causing contamination of watercourses or soakaways.

20 Wherever practical the Contractor shall use equipment to carry debris over a greater depth than one atmosphere and with a capability to suck liquid.

21 All arisings from the cleaning process shall be disposed of in an environmentally sensitive manner in accordance with current legislation.

Health and Safety

NOTE  The use of high pressure water can result in serious internal injuries that may not be apparent at the skin surface.

23 The Contractor shall ensure that all hoses are free from damage and that the equipment is in full working order.

NOTE Where overhead electric cables are present, there is a potential danger from accidental strike by a jet of water.

522 (mm/yy) Vortex Separators

1 Vortex separators shall be installed in accordance with the manufacturer's requirements and requirements stated in contract specific Appendix 1/10.

2 The formation level of the vortex separator shall be blinded with ST1 concrete in accordance with Series 2600.

3 The thickness of the concrete blinding shall be in accordance with the manufacturer's requirements and requirements stated in contract specific Appendix 1/10.

4 Vortex separators shall have no moving parts.

5 Internal components of the vortex separator shall be constructed from stainless steel and/or polyethylene.

523 (mm/yy) Grassed Surface Water Channels

1 For grassed surface water drainage channels a Type 5 or 6 fin drain in accordance with Clause 514 incorporating a double cuspated central impermeable core shall be installed at the edge of the pavement construction and in accordance with contract specific Appendix 5/3.

2 The double cuspated central core shall be made from polyethylene or polypropylene and in accordance with Clause 514.

3 The grassed surface water channel construction shall comprise of graded subsoil, a layer of topsoil and sub-surface drainage.

4 Prior to placing subsoil, the formation shall be ripped to a depth exceeding 150mm to provide a key between the existing ground and subsoil layer.

5 The subsoil shall be non cohesive.

6 The subsoil shall be free from stones larger than 50mm.

7 Where an impermeable membrane is required, the subsoil shall be free from flints.

8 Subsoil shall be placed in layers, not exceeding 100mm thick and compacted in accordance with Table 6/4 using a vibrating plate compactor Ref No. 4 Method 1 or Ref No. 2 Method 3.

9 The subsoil shall be shaped to the required channel cross sectional and longitudinal profiles stated in the contract specific Appendix 5/3.

10 Where stated in the contract specific Appendix 5/3, biodegradable geosynthetic reinforcement shall be placed between the subsoil and topsoil layers to provide support until the grass becomes established.

11 Fixings used to hold a geosynthetic in place shall not pierce the impermeable liner.

12 The surface material shall be topsoil class 5B in accordance with BS 3882 in contract specific Appendix 6/8 and the following:

1) The topsoil texture shall be a sandy loam or loamy sand

2) The topsoil shall have a pH greater than 5.5

3) The topsoil depth shall be between 35mm and 50 mm once compacted

13 Topsoil shall be compacted in accordance with with Table 6/4 using a vibrating plate compactor Ref No. 4 Method 1 or Ref No. 2 Method 3 but the number of passes shall be reduced to two.

14 A grassed surface water channel shall be seeded or lined with turf in accordance with this Clause.

15 The steps for seedbed or turfbed preparation shall be:

1) application of seedbed fertiliser at a ratio of 10:15:10 for N:P2O5:K2O at 30 g/m2; and

2) final raking or harrowing before seeding, hydroseeding or turfing in accordance with contract specific Appendix 5/3.

16 Where turf is used, it shall be placed immediately after compaction of the topsoil to minimise the risk of soil fines being washed away by surface runoff.

17 Where turf is used, an allowance shall be made for its thickness when defining the finished level of the topsoil.

524 (mm/yy) Combined Surface Water Channel and Pipe (Concrete)

1 Combined channel and pipe sections shall be constructed in accordance with Clause 1103 and contract specific Appendix 11/1.

2 Combined surface water channel and pipe sections shall be in accordance with contract specific Appendix 5/3.

3 The maximum pipe size for unreinforced mass concrete combined channel and pipe sections with a loading class of C250 and D400 shall be 300mm (Dmax), with a minimum vertical cover (Umin) of D/2, and a minimum horizontal cover (Hcmin) of D/2.

4 The maximum pipe size for light mesh reinforced concrete combined channel and pipe sections with a loading class of D400, shall be 400mm (Dmax), with a minimum vertical cover (Umin) of D/2, and a minimum horizontal cover (Hcmin) of D/2.

5 Light mesh reinforcement is a welded mesh made of steel bars compliant with BS 4483 and contract specific Appendix 5/3.

6 Light mesh reinforcement shall be placed horizontally in the base of the combined channel and pipe block such that the bars run parallel and perpendicular to the line of the pipe.

7 For light mesh reinforced concrete combined channel and pipe sections the minimum area of steel perpendicular to the longitudinal centre-line of the pipe shall be in accordance with contract specific Appendix 5/3.

8 The maximum pipe size for heavier mesh reinforced concrete combined channel and pipe sections with a loading class of D400, shall be 500mm (Dmax), with minimum vertical cover (Umin) of D/2, and a minimum horizontal cover (Hcmin) of D/2.

.9 Heavier mesh reinforcement is a welded mesh made of steel bars compliant with BS 4483 and contract specific Appendix 5/3.

10 Heavier mesh reinforcement shall be placed horizontally in the base of the combined channel and pipe block such that the bars run parallel and perpendicular to the line of the pipe.

11 For heavier mesh reinforced concrete combined channel and pipe sections the minimum area of steel perpendicular to the longitudinal centre-line of the pipe shall be in accordance with contract specific Appendix 5/3.

12 For mesh reinforced concrete combined channel and pipe sections the ends of the bars shall be left flat.

525 (mm/yy) Reservoir Pavements

1 If the use of reservoir pavements is proposed then the specification shall be submitted to the Overseeing Organisation for approval prior to construction.

526 (mm/yy) Maintenance Plans for Soakaways

1 The commissioning phase for soakaways shall be as described in contract specific Appendix 5/8.

2 The routine inspections required to determine the rate of accumulation of sediment in soakaways and pre-discharge treatment devices shall be as described in contract specific Appendix 5/8.

3 Based on the routine inspections and minimum monitoring requirements contained in contract specific Appendix 5/8, an asset specific inspection and maintenance plan shall be created for each soakaway.

The 'initial management plan' shall be the starting point for the asset specific inspection and maintenance plan.

4 The asset specific inspection and maintenance plan shall specify the frequency for future:

1) removal of debris from the floor of chamber and sediment traps (minimum annual frequency);

2) checking observation wells/inspection tubes for clogging;

3) checking that the soakaway is emptying;

4) inspecting the area around the soakaway for ground settlement or sediment loss;

5) removal and washing of exposed stones on the trench surface;

6) trimming any roots that may be causing blockages.

5 The inspection and maintenance plan(s) shall be submitted to the Overseeing Organisation to the timetable stated in contract specific Appendix 5/8.

508NI Gullies and Pipe Junctions

1 (mm/yy) Gullies shall be trapped, untrapped or sumpless as described in contract specific Appendix 5/1 and be in accordance with HCD Drawing Numbers F13 and F14.

All ST concrete referred to in this Clause shall comply with Clause 2602 unless otherwise described in contract specific Appendix 5/1.

2 Gullies shall be constructed so that no part of the spout or trap has a cross-sectional area less than 2/3rd that of the outlet. The depth of water seal in trapped gullies shall be not less than 50 mm.

3 (mm/yy) Precast concrete gullies and cover slabs shall comply with BS 5911-6 and clay gullies with BS EN 295. In situ concrete gullies shall be as described in contract specific Appendix 5/1 and constructed of ST4 concrete of 150 mm minimum thickness, using permanent or removable shuttering.

Where in situ concrete gullies are formed with permanent shuttering, such shuttering shall have current product acceptance scheme certification in accordance with sub-Clauses 104.15 and 104.16. Precast rectangular section gullies shall be as described in contract specific Appendix 5/1.

4 Gully gratings, kerb type gully covers and frames shall comply with BS EN 124: 1994 and the following and shall be of the classes and sizes described in contract specific Appendix 5/1.

5 (mm/yy) The upper surface of gully gratings shall be flat except where otherwise described in contract specific Appendix 5/1.

Slots in gratings or between gratings and frames shall not be orientated parallel to the direction of traffic except where the slots are less than 150 mm long or less than 20 mm wide. Minimum waterway areas shall be as specified in contract specific Appendix 5/1. Unless otherwise specified in contract specific Appendix 5/1, all gratings and frames shall be supplied in a fine cast (uncoated) condition. Where a coating is specified in contract specific Appendix 5/1, the coating shall only be applied when the surfaces of the casting are clean, free from rust and dry. Gully gratings shall be laid parallel to and 6 mm below the finished road surface. Hinged gratings shall be orientated to close in the direction of traffic flow. Frames shall be bedded on mortar complying with sub-Clause 507.21. Brickwork shall comply with sub-Clause 507.3.

6 (mm/yy) Backfilling to precast gullies shall be carried out up to sub-formation level with general fill material Class 1, as described in Table 6/1 compacted in compliance with Clause 612. Where mechanical compaction is impracticable, the backfilling shall be in ST2 concrete. The remainder of backfilling around gully shall be strength class C8/10 or ST2 concrete.

7 (mm/yy) Gully connection pipes shall be either flexible or rigid not exceeding 0.7 m in length with flexible joints for a distance of 2 m from the gully and shall be in accordance with Clause 507 when entering chambers. Junction pipes shall be manufactured of the same type and class of material as the remainder of the pipes in the run. Junction pipes which are laid but not immediately connected, shall be fitted with temporary stoppers or seals and the position of all such junctions shall be clearly defined by means of stakes or tracing wires properly marked or labelled.

Saddles may be used to form junctions only where permitted in contract specific Appendix 5/1. No internal projections greater than 5 mm will be permitted. Saddles for plastics pipes shall be installed in accordance with the manufacturer's recommendations.

Saddles with clay pipes shall be jointed with mortar designation (i) complying with Clause 2404, excluding lime. Saddles and pipes shall be surrounded with ST2 concrete.

8 (mm/yy) Where the adjustment or replacement of existing frames and gratings is required, the units shall be taken up and re-fixed or removed and replaced with new units complying with sub-Clauses 4 and 5 of this Clause, or as described in contract specific Appendix 5/1. On taking up or removal of the unit, any concrete or mortar bedding shall be broken out and the surface prepared. Where existing frames and covers or gratings are to be adjusted, the Contractor shall take up the unit and clean it so it is free from existing mortar, any debris, rust and is dry before re-use. The adjusted or replaced units shall be laid at a level, unless otherwise described in contract specific Appendix 5/1, 6 mm below the adjoining road surface on a mortar bed complying with sub-Clause 507.21. The finished thickness of the mortar bed shall be between 10 mm and 25 mm. Where required in contract specific Appendix 5/1, covers and gratings shall be bedded using a quick setting high strength mortar which shall have a declaration of performance for its intended use, the declaration of performance shall be provided to the Overseeing Organisation before use. Any additional adjustment shall be made by modifying the brickwork in compliance with sub-Clause 507.3 or by using a frame of suitable depth. On completion of the works, each grating shall be lifted and the frame and seating cleaned.

DC 5xx - Series 0500 NG Revision 1

NG 501 Pipes for Drainage and Service Ducts

NG 502 Excavation for Pipes and Chambers 6 3.

NG 503 Bedding, Laying and Surrounding of Pipes 7 4.

NG 504 Jointing of Pipes 8 5.

NG 505 Backfilling of Trenches

NG 506. Not Used.

NG 507 Chambers 11

NG 508 Gullies and Pipe Junctions 13 9.

NG 509 Testing and Cleaning 14 10.

NG 511 Land Drains 15 11.

NG 510 Surface Water Channels and Drainage Channel Blocks 16 12.

NG 512 Backfilling to Pipe Bays and Verges on Bridges 17 13.

NG 513 Permeable Backing to Earth Retaining Structures 18 14.

NG 514 Fin Drains 19 15. NG 515 Narrow Filter Drains 21 16.

NG 516 Combined Drainage and Kerb Systems 22 17.

NG 517 Linear Drainage Channel Systems 23 18.

NG 518 (mm/yy) Thermoplastics Structured Wall Pipes and Fittings

NG 519. Not Used

NG 520. Not Used

NG 521 (mm/yy) Low Pressure High Volume Jetting of Drainage Systems

NG 522. Not Used

NG 523 (mm/yy) Grassed Surface Water Channels

NG 524 (mm/yy) Combined Surface Water Channel and Pipe (Concrete)

NG 525 (mm/yy) Reservoir Pavements

NG 501 Pipes for Drainage and Service Ducts

1 Pipes can be made of materials that deflect relatively little under load before cracking (rigid pipes) or of materials that will tolerate large deflections under load before inward buckling occurs (flexible pipes).

Flexible joints enable either type of pipe to take up differential settlement within the ground.

2 (mm/yy) The specification includes a wide range of pipe materials. The Contractor should normally be offered in contract specific Appendix 5/1 the full selection of alternative pipe and bedding combinations determined in accordance with Advice Note HA 40 (DMRB 4.2.5) as detailed in the HCD for pipes up to 900 mm internal diameter. The required pipe stiffness and impact resistance for plastics pipes should be specified in contract specific Appendix 5/1. The requirements for thermoplastics pipes and fittings will normally be as in Clause 518 with raw material and quality control requirements as in NG 518.

Piped culverts up to 900 mm internal diameter should be specified in Series 500. Drains, box culverts, piped culverts (and other drains) of clear span or internal diameter exceeding 900 mm are subject to Overseeing Organisation's technical approval and should comply with Series 2500. A box culvert should not be specified where either a (concrete) box culvert or a (corrugated steel) piped culvert would be technically acceptable.

Wherever possible, the Contractor should be offered a choice and the Overseeing Organisation should be consulted during the scheme preparation. Box culverts, piped culverts (and other drains) of clear span or internal diameter exceeding 900 mm are structures subject to the Overseeing Organisation's technical approval. Care should be taken to ensure that there are no inconsistencies between any specific requirements included in an outline Approval in Principle form and the general requirements of Series 500. Where necessary, Contract-specific amendments should be included in Appendix 0/1 or 0/2 to achieve consistency.

Most of the pipes included in the specification will normally be satisfactory from the hydraulic flow capacity factor. However some products, especially corrugated pipes, can vary from the norm (eg clay/ concrete) and between manufacturers. The effect of a rougher pipe should be considered on the system as a whole and not just on the length in question. A pipe which is not acceptable on a straight exchange basis may be acceptable if diameters on adjacent lengths are adjusted. Contract specific Appendix 5/1 should provide the basis on which the Contractor is to submit his proposals for pipe types and makes.

3 (mm/yy) Any tendency to attack by acidic ground water or sulfates present in the backfill or the ground should be taken into account when the use of concrete, steel or iron pipes is being considered for inclusion in the schedule of acceptable alternatives in contract specific Appendix 5/1. The advice described in Clause NG 1704 should be considered regarding the risk of thaumasite sulfate attack on concrete used in drainage.

When acid soils (pH less than 6.5) are encountered, expert advice should be sought. There is some evidence that pipes made of sulfate-resisting cement will tolerate a pH as low as 6.0. The limiting value may be reduced to pH 5.5 when a bitumen coating is applied to the pipe. Sulfate attack on concrete is dealt with in Building Research Establishment Special Digest 1. More detailed information may be obtained from the manufacturers.

Protection to the lower third of the inside of corrugated steel piped culverts by means of an asphalt or in situ concrete coating will be required where stones and rocks are likely to be carried by the flow. Iron pipes are treated with a bitumen coating and have high durability in most soils, but when acid conditions are known to be present the additional protection of a polyethylene sleeve is desirable. Clay, GRP and PVC-U pipes are resistant to a wide range of groundwater chemicals.

4 For corrugated steel pipes of lock seam fabrication with a diameter not exceeding 900 mm, the specification of metal thickness should be given in contract specific Appendix 5/1. The tables issued by manufacturers recommend thicknesses corresponding to the diameter and depth of fill above the pipe.

5 Pipes of more than one type within any individual drain or service duct between consecutive chambers will be exceptional. Whatever the circumstance giving rise to the proposal, consideration should be given to whether the joint between the two pipes will provide an appropriately watertight joint and a smooth inner transition for rodding purposes.

6 Plastics pipes may deteriorate after a long period in sunlight. Where pipes have been manufactured and stored before being delivered to the Site, it may be necessary for the Contractor to cover them until they are installed.

7 (mm/yy) Any individual cable duct under a road may have to accept a power or a communication cable although these are normally placed in separate ducts.

Certain pipe materials have been excluded from the specification for use as ducts because cables cannot be readily drawn through them. Clauses NG 518, NG 1421 and NG 1530 give further information on the use of ducts for electrical work. Ducts should be scheduled in a similar way to pipes in contract specific Appendix 5/2. Any special requirements of Statutory Undertakers etc. should be stated clearly.

8 (mm/yy) Trenchless and minimum dig installation is the means of installing, replacing and renovating pipes, ducts and small tunnels with minimal or no excavation from the surface. MCHW 5, Series 8000 covers the requirements for trenchless and minimum dig installation of highway drainage, service ducts, sleeves and culverts up to and including 900 mm nominal internal diameter or width. The information required from the designer/compiler that will detail the performance required from the trenchless installation should be given in NG Sample Appendix 80/1 (MCHW 5.8.3).

NG 502 Excavation for Pipes and Chambers

1 In the preparation of contract specific Appendix 6/3, it may be considered appropriate to permit battering of slopes where this would not affect adversely the permanent works or the basis of structural design of the pipe/ trench.

2 (mm/yy) In the event of excavation to a greater depth than necessary the Contractor is obliged to reinstate.

The use of ST1 concrete to remedy excess excavation should be restricted to areas where compaction is impracticable. Where the floor of the trench passes through a localised area of disturbed and uncompacted soil or softened clay further excavation and replacement with appropriate material may be required to allow pipe laying to proceed.

3 Where pipes are to be installed beneath heavily trafficked existing roads, etc, where it is undesirable that the existing ground surface should be disturbed, consideration should always be given to the possibility of inserting the pipe by suitable thrust boring or jacking processes.

NG 503 Bedding, Laying and Surrounding of Pipes

1 (mm/yy) Pipe bedding material should be readily obtainable since a wide range of gradings and sizes complying with BS EN 13242 are permitted. Pipe bedding material needs to flow readily and compact uniformly, thus a low coefficient of uniformity is necessary. In order to make savings in coarser granular materials a sand bed may be adopted. Surround to pipes should be in bedding material or acceptable material (Class 8) as appropriate to the alternatives shown in the HCD. Coarse granular material may consist of natural aggregate, recycled coarse aggregate, recycled concrete aggregate, artificial or blended combinations of these aggregates, which satisfy the requirements of the specification.

2 (mm/yy) The limiting values in sub-Clauses 503.4 and 503.5 have been chosen to ensure that problems do not occur due to oxidation of reduced sulfur compounds such as pyrite. Further guidance is given in sub-Clause NG 601.8 and Clause NG 644.

3 (mm/yy) A distinction is to be made between the requirements of bedding, haunching and surrounding and those of backfilling. The former comprise all operations of trench fill up to a level 300 mm above the top of the barrel of the pipe. Backfilling constitutes the remaining operations up to ground level in verges and open ground and up to formation or sub-formation level under carriageways. Work above formation level constitutes construction or reinstatement of the pavement (see NG 706).

4 (mm/yy) Concrete surround should be used exceptionally, eg for protection of pipes against mechanical damage from subsequent operations after construction of the pipeline and where remedial measures due to over excavation are required.

Protection of existing pipes where necessary may take the form of a concrete arch or slab above the pipe.

NG 504 Jointing of Pipes

1 Pipe joints for surface water drains, unlike foul drains, do not always have to be completely watertight.

Small amounts of seepage as allowed in sub-Clause 509.7 can be tolerated particularly where pipes are laid in cuttings or below the water table.

However, joints in pipes in soils that are predominantly fine sands or coarse silts should have watertight joints to prevent soil particles passing through the joint into the pipe leaving voids on the outside of the pipe. Where fine sands or coarse silts might be a problem but the more expensive rubber ring flexible joint is unwarranted, consideration can be given to certain proprietary wrap type joints that are available. These may also be specified where root penetration needs to be prevented. Requirements should be given in contract specific Appendix 5/1.

2 Most watertight joints will be flexible joints although rigid joints are occasionally used on clay pipes. In and under embankments, or if differential settlement is expected in compressible soils subject to non-uniform loading, then flexible joints and (except for pipes below the water table laid in non-erodible soils) watertight joints should be specified. The maximum length of pipe between flexible joints may have to be limited where considerable movement is expected. The limits of the exclusions should be shown in contract specific Appendix 5/1.

3 Culverts are generally considered to be drains but they do not necessarily require watertight joints.

Where watertight joints are required for culverts this should be stated in contract specific Appendix 5/1.

NG 505 Backfilling of Trenches

1 (mm/yy) Type A material is intended for sub-soil drainage. The Specification permits a wide grading envelope from BS EN 13285 so that local sources may be used as far as possible. When soils to be drained require a particular grading of filter aggregate it can be specified under the heading Type C in Table 5/5. The design should be based on knowledge of local sources of supply, BS EN 13285 and Transport and Road Research Laboratory Report LR 346 which gives guidance on the design of filter materials. Type B material is a coarse aggregate complying with BS EN 13242, intended for use where the drain is designed to intercept surface water flowing to the pipe.

Grit from the carriageway may slowly block this type of filter and it may require cleaning or replacement periodically. Where filter drains are located close to carriageways and are likely to be overrun by traffic, methods of preventing the problem of 'stone scatter' should be considered. Some possible solutions are shown on HCD Drawing Number B15.

2 (mm/yy) The limiting values in sub-Clauses 505.4 and 505.5 have been chosen to ensure that problems do not occur due to oxidation of reduced sulfur compounds such as pyrite. Further guidance is given in sub-Clause NG 601.8 and Clause NG 644.

3 (mm/yy) Filter drains can be constructed by machines that excavate the trench, support the sides, lay the pipe and backfill with filter material in one operation. The trench is normally constructed with a semi-circular floor providing a most effective support to the pipe without further bedding. As contamination of the filter material is minimized by the supporting shutter attached to the machine a much narrower trench than that achieved by conventional excavation is possible.

5.4.1 (mm/yy) Where geotextile membranes are specified to be in accordance with Clause 609 the compiler should use contract specific Appendix 6/5 to detail the performance requirements for the geotextile.

NG506. Not Used

NG 507 Chambers

1 (mm/yy) Concrete chambers, precast or cast in situ against forms, do not require strengthening with additional concrete surround. Access shafts in precast concrete should be strengthened, however, as a protection against loads from backfilling operations.

Brick chambers, including shafts do not need a concrete surround for strengthening. It may however be necessary to backfill with concrete where space is insufficient to permit compaction of one of the earthwork's acceptable materials. Inspection chambers are those that can be maintained from the surface and do not need to be entered. The types of brick to be used for brick chambers, and beneath chamber frames, in normal circumstances are specified in Clause 2406.

Where a different type of brick is required this should be described in contract specific Appendix 24/1.

Any brickwork upon which chamber frames are seated should be properly constructed.

2 (mm/yy) Safety precautions require that chamber covers have a minimum opening as shown on the HCD Drawings where personnel may be required to enter completely. In carriageways, hard shoulders and verges, chamber covers, frames and gratings should be at least Class D400. Where, exceptionally, covers have to be located in areas subjected to large numbers of high speed heavy goods vehicles, Class E600 chamber covers, frames and gratings should be considered.

Advice may be sought from the Overseeing Organisation. It will normally be expected that the minimum frame depth is 150 mm. When specifying cover types, Compilers should have regard to the weight of each element of the cover so that it could be lifted safely and should review the measures available to prevent covers falling into the chamber when being removed. Reference should be made to the HSE Manual Handling Operations Regulations and guidance, where appropriate.

Seating of covers within frames is not required unless specified in contract specific Appendix 5/1.

3 It may be necessary, due to constraints in pipe lengths to vary the lengths of the articulated section described in sub-Clause 507.9. However, the principle of having the joint nearest the chamber as close as possible to the chamber and the next joint positioned so as to give an effective length of intervening articulated pipe, free from constraint by the trench bottom, should be maintained.

4 (mm/yy) BS EN 124 makes no reference to coatings.

Many manufacturers apply a coating in order to prevent discolouration of the castings while in stock or in transit. However, BS 7903 : 1997 states that short term coatings offer no lasting product enhancement and any surface oxidation of the cast iron has no detrimental effect upon its use.

5 (mm/yy) It is essential that the in-service skid resistance of a cover is suitable for the conditions of use.

The site categories given in HD 28 (DMRB 7.3.1) should be used as guidance. To convert the SCRIM Coefficient (SC) figures given in HD 28 to the Polished Skid Resistance Value (PSRV) given in BS 9124 the following formula can be used.

PSRV= (SC + 0.05) x 100 It is important to note that the skid resistance of the cover in use will depend upon a number of factors.

These factors might include the material from which the cover is made, the type of pattern on the surface of the cover in use, the type of trafficking that the cover is subjected to, environmental conditions etc.

The actual skid resistance of the cover in use at any point in time is likely to be different from that obtained on the cover at the point of manufacture or installation.

Where a specified level of skid resistance in use is required then it is important that a cover is selected that can withstand the trafficking expected at a particular site so that the level of polishing does not reduce the frictional properties of the cover to a level below that required.

The Unpolished Skid Resistance Value (USRV) and/or the use of a pattern on the surface of the cover does not in itself ensure satisfactory levels of skid resistance for all situations of use.

(mm/yy) The use of proprietary bedding components of different specifications may be permitted subject to them being demonstrated as equivalent and meeting the requirements stated in Clause 104.

Reinstatement of Surrounding Flexible Carriageway

(mm/yy) Where the space between the frame and the sides of the excavation at all levels is inadequate for mechanical compaction equipment, a proprietary self-setting fill material compatible with the bedding material may be used when installed to the manufacturer's instructions.

NG 508 Gullies and Pipe Junctions

1 (mm/yy) Trapped gullies are essential only on connections to combined or foul drains in urban areas or on roads where traps are regularly and frequently emptied. In terms of pollution there is little difference in water quality between the flow through trapped or untrapped gullies although a trapped gully would normally retain the contents of a vehicle's sump in the event of an accident. Further advice on sumpless gullies can be found in HA 105 (DMRB 4.2.3).

2 Where concrete trapped gullies are cast in situ using a permanent plastic mould, the part forming the trap should be equal in all respects to that of precast concrete or clay gullies.

3 Any brickwork upon which gully frames are seated should be properly constructed.

NG 509 Testing and Cleaning

1 Requirements for drain testing should be specified in contract specific Appendix 1/5. The air test does not indicate the location of any large leaks that may be present. A water test may follow the failure of an air test.

2 Fall of the test water level may be due to one or more of the following causes:

1) Absorption by pipes or joints.

2) Excessive sweating of pipes or joints.

3) Leakage from defective pipes or joints or plugs.

4) Trapped air.

Some pipes absorb more water or trap more air at the joints than others. Allowance should be made for this by adding water to maintain the test head for appropriate periods. While the aim should be to commence the test period proper 2 hours after filling, the appropriate period may best be determined by conferring with the pipe manufacturers.

3 (mm/yy) When checking pipelines, Closed Circuit Television (CCTV) inspection is a suitable alternative to the mandrel test. However, CCTV inspection should always be used on foul sewers and connections to sewers. To avoid subsequent disputes it is essential to liaise with the drainage authority when checking connections to existing sewers to ensure acceptability of the work and to determine the extent of the survey required on existing sewers.

4 The test for partly watertight joints must be carried out before the pipe is laid because the water escaping from the joint has to be measured. The purpose of the test is to prove that the joint does not leak so excessively as to cause piping in any granular surround.

5 (mm/yy) Series 9000 (MCHW 5.9, Parts 1 to 5) contains the documentation for the specialist activity of the CCTV survey of highway drainage systems. The specification covers all types of pipes with diameters up to and including 900 mm including sub-surface drainage and other non-piped systems that are being introduced.

Pipes and conduits in excess of 900 mm are classified as structures that require technical approval; however, this technique is equally applicable to the remote inspection of these structures up to 1800 mm diameter.

6 (mm/yy) When checking foul drains and their connections to existing sewers, it is essential to liaise with the drainage authority to ensure acceptability of the work and to determine the extent of the survey, including CCTV survey, required.

NG 511 Land Drains

1 New highway construction works are likely to disturb and render ineffective existing drainage systems in adjoining land; it will therefore be necessary for the Contractor to carry out without delay any such temporary or permanent remedial works as may be described in contract specific Appendix 5/1.

The ideal arrangement for land drainage remedial works is that the system of drainage of land adjoining the road should be separate from the road drainage so that the reinstatement of the system is on the owner's land and the matter falls to be dealt with by the District Valuer as a matter of accommodation works. When such arrangements are not practicable or the cost is excessive, the existing land drainage system should be linked with the drainage system of the road.

NG 510 Surface Water Channels and Drainage Channel Blocks

1 (mm/yy) Requirements for these should be included in contract specific Appendix 5/3 and be compatible with the relevant HCD Series B and Series F drawings.

NG 512 Backfilling to Pipe Bays and Verges on Bridges

1 Any special filling material, eg. lightweight material, should be described by providing additional information on the drawings, cross-referenced in contract specific Appendix 5/1.

NG 513 Permeable Backing to Earth Retaining Structures

1 For granular backing, Type C has been added to allow for the design of a filter compatible with the particular type of filling to be employed adjacent to the structure. It is recognised that the use of Type A will not always meet the piping and permeability ratio criteria.

2 Fin drains are not allowed as permeable backing to structures because it is not yet possible to demonstrate that any of them will have the required design life of 120 years.

NG 514 Fin Drains

1 These consist of a core which will allow the free drainage of water entering through geotextile filters on the outside of the core. The core may consist of nets, webs, grids or preformed plastic sheets or strips. Some restrict entry through one side or confine water entering to part of the cross-sectional area of the core. Any such restrictions should be taken into account in assessing the flow characteristics of the drain. Fin drains are intended to be used for subsurface drainage, as shown in the HCD, to remove and keep out water from the road structure. They are provided to remove surface infiltration from the pavement layers, to prevent infiltration from shoulders, medians and verges into the pavement, and sometimes to cut off shallow groundwater seepage. They thus act as low-capacity filter drains. In normal circumstances, the Contractor should be permitted the choice of any of the types shown in the HCD. If however, for engineering reasons, exclusion of a particular type is required, this should be stated in contract specific Appendix 5/4. The minimum values for mechanical and hydraulic properties given in Clause 514 are intended for this particular usage and may not be relevant to fin drains used elsewhere.

Additionally, the Clause requires specification of the pore size distribution of the geotextile and the inflow and discharge capacity of the fin drain determined for the site conditions.

2 The pore size for the geotextile should be selected using filtration criteria to be compatible with the adjacent soil or construction layer in order to prevent the occurrence of piping. The following soil retention criteria may be used in determining O90. Other criteria are available.

TABLE NG 5/14 Uniformity Coefficient of d60/ d10 Soil Woven and Meltbonded Geotextiles Needle-punched Geotextiles

| Uniformity Coefficient of d60 / d10 | Soil Woven and Meltbonded Geotextiles | Needle-punched Geotextiles |
| --- | --- | --- |
| 1 to 5 | O90/d50 = 1 to O90/d50 = 3 | O90/d50 = 4 to O90/d50 = 6 |
| > 5 | O90/d90 < 1 or O90/d50 < 3 | O90/d90 < 1.8 or O90/d50 < 6 |

NOTE 1 dn = n% size in base soil (n% is finer)

NOTE 2 O90 = 90% opening (pore) size of geotextile

NOTE 3 (90% of openings are smaller)

In general, it will be sufficient to specify only the maximum value of O90 that will satisfactorily retain the adjacent soil particles as the minimum O90 size will be governed by the permeability requirements in sub-Clause 514.4. Geotextiles will usually be in contact with variable surface soil deposits, as well as the more uniform materials composing the pavement, and great accuracy in specification may not therefore be feasible.

The finest O90 relevant to the various soil deposits likely to be encountered may be specified. An O90 value of 1 mm should be considered as the upper limit even with large grained soils. With cohesive fine grained soils such as clays the use of the above criteria will result in such small pore sizes that sufficient water flow cannot be obtained. In such cases the cohesion of the soil particles themselves is relied upon to prevent piping and a maximum O90 value of 250 microns may be chosen.

Dispersive silts can present particular problems and in these cases the O90 value may be less than 250 microns: however, the value to be specified should be carefully considered in order both to avoid piping and to ensure sufficient long-term flow.

3 (mm/yy) Sub-Clause 4 of Clause 514 requires the designer to specify the flow rate normal to the geotextile wrapping to the filter drain. The specified flow rate should incorporate a margin of safety to allow for the impeded flow due to the adjacent core of the fin drain (or the filter material in a narrow filter drain) as described in sub-Clause 13 of Clause 514. It should also incorporate a substantial margin to allow for the reduction of flow with time due to clogging. The long-term flow through a geotextile in contact with the coarse gravel may not differ significantly from the short-term flow measured in the standard test. In contrast, the long term flow through a geotextile in contact with a dispersive silt may be one thousand times smaller than the short-term flow. There is some evidence that chemical or biological leachates may also cause severe clogging.

Different rates of flow into the two sides of the fin drain may be specified, for example, if the water flows from the verges are expected to be very different to those from the pavement structure. A value of 10 litres/m2/sec is suggested for use against the unbound mixture for subbase and capping specified in Series 600 and 800.

Very much smaller values are adequate for soils and backfills other than coarse gravels, and possibly dispersive silts or contaminated sites. It should be appreciated that, because of such long-term effects, these flow rates should not be used to determine the in-plane design requirements of the fin drain.

4 Clause 514 requires specification of the in-plane flow capacity of the fin drain. This design capacity should allow for infiltration through the pavement and verges and any other source of ground water ingress. Until more accurate means of establishing infiltration rates through the pavement are available a value not less than the mean intensity of a one year 2 hour rainfall should be assumed. The fin drain Type 5 of Drawing F18 in the HCD acts both as a filter drain and a carrier pipe. Thus in-plane flow must be specified for flow both along the drain parallel to the road edge and near-vertically down the drain.

For all other drain types, only near-vertical downward flow need be specified. Fin drain Type 10 in Drawing F21 should either have an impermeable side or be covered by an impermeable membrane unless no significant blocking of the core will occur during the slip-forming of the channel.

Fin drains are normally laid at constant depth below the carriageway and their gradient will therefore follow that of the road. Drainage capacities should be designed for these gradients and outfall lengths determined accordingly. For drain Type 5 the flow rates that are stated in contract specific Appendix 5/4 should be the capacity required linearly extrapolated to the standard gradients in Table 5/8. Where fin drains utilise a pipe, capacities may be obtained from hydraulic tables and the required diameter specified.

5 Sub-Clause 9 of Clause 514 specifies the use of as-dug material for trench backfill. If this material when compacted is sufficiently less permeable to affect the efficiency of the drain, or contains stones larger than about 100 mm which could damage the drain, an alternative material compatible with the geotextile should be used.

6 Proper functioning of the fin drain and its ancillary components depends critically on adequate installation and joining procedures.

Fin drains can be problematical during construction phase for the following reasons:

1) (mm/yy) They do not provide immediate drainage for the unpaved subbase.

2) They are not designed for surface water flows.

3) Fine particles transported by surface water or vehicles may clog the filter or silt the drain.

4) They may be damaged by the passage of construction traffic.

Appropriate protection measures must be taken, eg polythene sheeting, temporary drainage channels, or warning fence. Alternatively, the drains may be installed towards the end of the construction phase.

7 Fin drain components that fall under the scope of the Construction Products Regulation are required to have a declaration of performance in accordance with the relevant harmonised standard. All fin drains must be the subject of product acceptance scheme certification which certifies the values achieved for the specified properties when tested in accordance with Clause 514. Fin drains are available in a variety of configurations with different types of core structure. It is intended that whenever the Contractor proposes the use of any fin drain he must supply copies of the appropriate product acceptance scheme certificate(s) to confirm that the product complies with the contract requirements.

(Further guidance may be sought from the Overseeing Organisation.) 14.17 The Contractor should be offered a selection of fin drain types from a list of acceptable alternatives (see HCD Drawing F18) listed in contract specific Appendix 5/4.

NG 515 Narrow Filter Drains

1 Narrow filter drains are intended for use as edge of pavement sub-surface drains and are suitable alternatives to fin drains for this purpose. Both types have the same requirements of performance and the guidance given in NG 514 is equally applicable to determining the soil retention and permeability criteria of the geotextile used in narrow filter drains and to the discharge capacity of the drain. In normal circumstances, the Contractor should be permitted the choice of any of the types shown in the HCD. If however, for engineering reasons, exclusion of a particular type is required, this should be stated in contract specific Appendix 5/4.

2 In drain Type 8 the filtration function is achieved by a granular filter material and geotextile sock and in Type 9 by means of a geotextile wrapping to the drain.

Both filters should be designed to be compatible with the adjacent soil or construction layer. For the Type 8 drain granular material the category for tolerances at mid-size sieves should be specified in contract specific Appendix 5/4 . The geotextile sock round the pipe is a second stage filter where it is required to retain the particles of the first stage granular material. However, the pipe when laid in the narrow trench may have insufficient granular surround for fully effective first stage filtration to be achieved. Pore sizes for the sock material should therefore be designed to also retain the finer soil particles outside the trench.

3 The specification for granular material in Table 5/8 is intended to permit the widest range of available material to be used. These limits have been set to reduce the risk of damage to the geotextile, to avoid gap grading of the filter material and to ensure an adequate degree of permeability. For the material as specified a minimum value of permeability of about 1 x 10-4 m/second which is similar to that obtained by a clean coarse sand may be assumed. A higher permeability will rarely be necessary but if required it may be specified in contract specific Appendix 5/4.

4 Narrow filter drains require protection during the construction phase similar to that provided for fin drains (see NG 514.6).

5 The geotextiles used in narrow filter drains are required to have a declaration of performance in accordance with the Construction Products Regulation and harmonised standard BS EN 13252.

NG 516 Combined Drainage and Kerb Systems

1 The Drawings should show the location and gradient(s) of the combined drainage and kerb system, the position of access, silt trap, outfall and end units together with the position and invert level of the surface water outfall connection. The position of any movement joints required in the system, eg. at joints in bridge decks or concrete carriageways, should be shown.

Details of any ducts, cabling, etc, required to pass under the kerb should be shown. The extent of the work to be designed by the Contractor should be clearly defined.

2 Combined drainage and kerb systems should be scheduled in contract specific Appendix 1/10 and cross-reference made to the design requirements given in contract specific Appendix 5/5.

3 (mm/yy) Advice on the location of Class C and Class D systems is given in sub-Clause NG 517.1.

NG 517 Linear Drainage Channel Systems

1 (mm/yy) The linear drainage channels specified in Clause 517 may be used in trunk roads including motorways. Class D channels are designed to withstand loadings of all types of road vehicle that are permitted on trunk roads including motorways. Class C channels should only be installed in locations which are protected from direct traffic loading, eg. in areas behind safety barriers. The range of slot dimensions permissible within Clause 517 is not compatible with safe usage by cyclists and pedestrians, and units with slot dimensions described in Clause 517 should not be used in areas subject to such traffic.

2 The drawings should show the location of the linear drainage systems and the positions of the surface water outfall chambers into which the systems are to outfall. The position of any movement joints required in the system, eg. at joints in bridge decks or concrete carriageways, should be shown.

Details of any ducts, cabling, etc., required to pass under the systems should be shown. The extent of the work to be designed by the Contractor should be clearly defined.

3 Linear drainage channel systems should be scheduled in contract specific Appendix 1/10 and cross reference made to the design requirements given in contract specific Appendix 5/6.

4 Variations to stated dimensions may be considered providing that the product will meet the requirements of this specification.

5 A system comprising units which may be otherwise too small to accommodate design flows without surcharge may be acceptable in conjunction with the provision of additional intermediate or upstream chambers subject to the following requirements:

1) Intermediate chambers should be compatible with the standards of the chambers shown on the drawings and any longitudinal drains connecting such chambers should also be connected into the intermediate chambers.

2) Not more than one intermediate chamber should be permitted between the upstream and downstream chambers of any drain shown on the drawings.

3) Not more than one additional chamber should be permitted upstream of each upstream chamber shown on the drawings.

NG 518 (mm/yy) Thermoplastics Structured Wall Pipes and Fittings

General

1 Where thermoplastics structured wall pipes and fittings are included in the schedules of permitted alternatives in contract specific Appendix 5/1, the material properties required of the different pipe materials should be specified by the manufacturer in the format given in contract specific Appendix 5/7.

The third party certification body verifies these properties against the declared specification.

Fulfilment of the performance requirements in conjunction with maintaining the material specification should provide the required durability for the product (ie a minimum life of 45 years).

Materials

2 Most thermoplastics are stable against common chemicals found in ground water and in surface water runoff. The pipes and fittings should be protected against prolonged exposure to sunlight and it may be necessary for the Contractor to cover the pipes prior to installation.

Dimensions

3 Dimensions should be measured in accordance with BS EN 476 and should fulfil the requirements of sub-Clause 518.3 and the declared specification (see contract specific Appendix 5/7).

Appearance

4 The bore of the pipe fittings should be smooth to allow the correct choice of Manning's coefficient for hydraulic design of the system.

Structured Wall Pipe

5 Table 5/9 gives the requirements for structured wall pipes. Where reference is made to British, European or International Standards, these standards should be consulted to discern the relevant test conditions for the product. Where no standard test method is available, the test method is described in sub-Clauses 518.11 to 518.13. Additional information, is given in Table NG 5/1.

TABLE NG 5/1 (mm/yy) Additional Information for Structured Wall Pipe

| Property | Additional Information |
| --- | --- |
| General | Quality control and identification |
| Ring stiffness | 6 kN/m2 minimum. Lower stiffness values are permitted if design calculations to BS EN 1295-1 (UK national annex), based on site specific installation conditions, indicate satisfactory performance). Manufacturer's minimum specification is required for calculation to BS EN 1295. |
| Creep Ratio | Manufacturer's maximum specification is required for calculation to BS EN 1295. Note: the long term ring stiffness used for design purposes is the two year stiffness and is calculated1 by dividing the ring stiffness by the creep ratio. |
| High volume low pressure jetting | A pass is deemed to also establish satisfactory performance at high volume and low pressure. |
| Longitudinal bending | To reduce the possibility of problems caused by handling on site. |
| Impact resistance at 0°C | The d50 striker is non-standard. |
| Impact resistance at 23°C | For quality control only. |
| Rodding resistance | To simulate effects of drain rodding. |
| Creep at elevated temperature (ducts) | To simulate the effect of exposure to high temperatures that may occur in power cable ducts. |
| Resistance to point loads (ducts) | Simulate sharp aggregate penetration. |

Note 1: When carrying out calculations to BS EN 1295 the minimum value for stiffness and the maximum value of creep ratio should be used in order to establish the long term stiffness. For example, a pipe might have a declared minimum stiffness of 4.5 and a maximum declared creep ratio of 3.8. The long term stiffness would be 4.5/3.8 = 1.18 kN/m2. Site-specific calculations, in accordance with BS EN 1295, can be used to establish that the long term deformation will be less than 5% and the safety factor against buckling greater than two.

Fittings

6 As stated in sub-Clause 5 of this Clause the standards should be consulted to discern the relevant test conditions for the product against the requirements given in Table 5/10.

Installation and Handling

7 (mm/yy) Care should be taken to prevent changes in line or level when placing the surround material over the pipe crown, as there is the possibility of flotation (see also sub-Clause 503.6). Compaction levels of all sidefill and backfill material must be closely monitored as these have a direct impact on the ground settlement and pipe deflection characteristics. Special precautions may be necessary where the system is subject to high construction loading such as spreader plates.

8 Installation and compaction of the pipe and surround are key to the performance and durability of the system. The pipe must be installed to line and level and any pipe that is out of shape should not be installed.

The change in shape could be caused by, longitudinal bending, mechanical damage or deformation under lifting and installation. Larger diameter pipes and fittings must be handled with care as they are more likely to suffer impact damage especially at lower temperatures. Reference should be made to the HSE Manual Handling Operations Regulations and guidance, where appropriate, and care whilst using mechanical plant especially near to trench walls. The manufacturer must supply the weight per metre of the pipe and from this information the Contractor is able to assess the lifting needs for installation of the pipe.

Test Method for Longitudinal Bending

9 The test is intended to eliminate very flexible pipe (eg coilable pipe) and pipe which is so weak that it might deform whilst being handled on site.

10 The two level support blocks at least 250 mm wide and of sufficient height to allow the pipe to sag over its length without touching the ground could consist of standard building blocks stood on their ends.

Test Method for Rodding Resistance (Internal Puncture)

11 The test is intended to simulate damage which might be caused by the ferrule of a drain cleaning rod being impacted against the inside of the pipe or fitting during cleaning operations and is intended to ensure the structural integrity of the inner layer. A segment of pipe or a section from a fitting is subjected to impact on its internal surface whilst fully supported by its external surface.

Test Method for Resistance to Sharp Objects

12 The test is intended to simulate the effect of penetration due to sharp aggregate and is intended to exclude ducts with particularly thin wall section.

NG 519. Not Used

NG 520. Not Used

21. NG 521 (mm/yy) Low Pressure High Volume Jetting of Drainage Systems

General

1 The drainage system to be cleaned should be stated in contract specific Appendix 5/1. The details should include the locations, type of pipe material, where known, pipe diameter or state the type of system if not piped.

2 Where pitch fibre, porous concrete or perforated pipes are known to be present, these should be identified in contract specific Appendix 5/1 and the Contractor made aware of their presence.

3 If the works are required to be detailed in accordance with contract specific Appendix 90/1 of Series 9000 (MCHW 5.9.3), the Compiler's attention is drawn to the need to ensure also that the relevant sections of the Method of Measurement for the Series 9000 are included (and amended if necessary) within the scheme specific documents.

Jetting of Piped Drainage Systems

4 An alternative method of cleaning should be used for porous concrete or perforated pipes. There is a risk to the structural integrity of the porous pipes and a risk that exfiltration will enter the unbound pavement layers and wash out fine material in both instances. This may cause voids to form and result in premature pavement failure. Pitch fibre pipes should be treated as "unknown/ structurally damaged" in accordance with Table 5/12.

Jetting of Linear Drainage Systems

5 The type of linear drainage system should be detailed in contract specific Appendix 5/1.

6 The use of a high pressure lance may be used externally to clear gratings or slots of linear drainage systems.

Silt Removal

7 The pipeline should be deemed to be clean when the silt content of the cross-sectional area of the pipe is between 0 and 10% for pipes ≤600 mm and between 0 and 5% for pipes >600 mm diameter.

Health and Safety

8 (mm/yy) The safety aspects to be addressed relating to jetting are, practices concerning high pressure water, possible infection from the drain contents, working on the highway and in some circumstances, working in confined spaces.

Equipment

9 Jet heads with nozzles set at approximately 20o to the pipe surface have a low jet angle and are unlikely to cause damage to the pipeline. Fan jets have low jet angles and are widely dissipated and hence unlikely to cause damage to the pipeline.

NG 522. Not Used

NG 523 (mm/yy) Grassed Surface Water Channels

1 Grassed channel construction should be undertaken in early spring or early autumn to avoid long establishment times in winter and hot/dry periods in summer.

2 A geo-grid is usually held in place by U-shaped steel pins or staples.

3 During construction of the channels, temporary measures may be needed to prevent surface runoff from the pavement or verge washing away the topsoil or surcharging the fin drain.

4 Topsoil deeper than 50 mm will encourage the growth of weeds and other forms of vegetation.

5 Turfing offers advantages over hydro-seeding in that it will give a much greater level of initial protection to the topsoil and hydro-seeding is dependent on the quality of the seed mixture and the fibre reinforcement.

6 Where the channel is seeded directly, a minimal depth of topsoil (but within the specification) will enable the grass roots to penetrate the subsoil and bond the two layers together.

7 Compiler to select grass mix based on options in CD521 Appendix J.

NG 524 (mm/yy) Combined Surface Water Channel and Pipe (Concrete)

1 To complete contract specific Appendix 11/1 for Combined Surface Water Channel and Pipe (Concrete)

NG 525 (mm/yy) Reservoir Pavements

1 During construction, reservoir pavements should be protected from construction debris and soil-contaminated storm water runoff from other parts of the site.

2 Debris and sediment laden runoff generated during construction can cause clogging of the reservoir pavement.

3 Reservoir pavements should be built late in the construction schedule when most of the earthworks, including grading and landscaping, are complete.

4 If it is not possible to programme construction of reservoir pavements late in the works, specific measures may be required to isolate and protect the reservoir pavement.

5 Where a reservoir pavement requires repair or reinstatement, materials shall be replaced on a like for like basis.

6 The repair technique to be adopted depends on the degree and extent of the degradation.

7 For surface damage limited to a few square metres, for example in the event of incidents of pollution or fire, repair of pervious surfaces may be carried out using conventional materials.

25.8 When damage is localised and limited to loss of material by fretting under traffic, or gouging as a result of an accident, it is not generally necessary to intervene.

9 If it is necessary to maintain the existing pervious nature of the pavement, the damaged surfacing material should be removed and repaired.

10 Planing or cutting may be used in removal of the damaged surface.

11 Vertical joints should be prepared by application of a suitable bonding agent before repair.

Series 0500 Contract Specific Appendices

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/1: (mm/yy) DRAINAGE REQUIREMENTS

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/2: (mm/yy) SERVICE DUCT REQUIREMENTS

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/3: SURFACE WATER CHANNELS AND DRAINAGE CHANNEL BLOCKS

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/4: FIN DRAINS AND NARROW FILTER DRAINS

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/5: COMBINED DRAINAGE AND KERB SYSTEMS

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/6: LINEAR DRAINAGE CHANNEL SYSTEMS

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/7: (mm/yy) THERMOPLASTICS STRUCTURAL WALL PIPES AND FITTINGS

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/8: (mm/yy) MAINTENANCE PLANS FOR SOAKAWAYS

1. NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/1: (mm/yy) DRAINAGE REQUIREMENTS

NOTE [Note to compiler: This should include:]

1 (mm/yy) the basis of the hydraulic design of the system on which the Contractor should submit his proposals for pipe types and makes [501.3, 8005.1];

2 (mm/yy) a schedule of permitted alternative pipe and bedding combinations; [which should be determined in accordance with Advice Note HA 40 (DMRB 4.2.5)] [503.3, 8005.7] and list of pipelines to be constructed other than in a trench [608.8];

3 (mm/yy) grading and geometrical requirements for filter drain material Type C;

4 values of pipe stiffness class, creep ratio and impact resistance for thermoplastics pipes; 1.5 5 plate thicknesses for bolted segmental plate pipes [501.4(i)] and minimum plate thickness for corrugated steel pipes of lock seam fabrication if different from sub-Clause 501.4;

6 whether corrugated steel pipes are to have additional protection of hot-applied bitumen [501.5];

7 where sulfate-resisting Portland cement is required for concrete pipes [Table 5/1];

8 pipe classification to BS EN 14364 and BS EN 1796 for GRP pipes for drainage [Table 5/1];

9 laying method for corrugated coilable perforated pipes [503.2]

10 details of materials if differing from the requirements of sub-Clause 503.3(v);

11 (mm/yy) whether joints in surface water drains should be watertight or partly watertight [504.2];

12 where rigid joints may be used [504.3]

13 (mm/yy) backfilling requirements differing from sub-Clause 505.2; references to drawings giving locations where backfilling is required to a level other than that specified in sub-Clause 505.8;

14 where saddles may be used [508.7 and 508.7NI]

15 material classification for backfilling filter drains and permeability requirements including test details [509.8];

16 (mm/yy) references to drawings showing requirements for connecting existing drains to new drains and details of special connecting pipes [506.1, 8005.19];

17 requirements for sealing, removal or grouting of existing drains [506.3];

18 details of connecting existing land drains [511.1];

19 whether severed mole drains are to be intercepted by construction of a land drain [511.4];

20 requirements for backfilling mole channels if different from the requirements of sub-Clause 511.4;

21 references to drawings which show chamber types [507.1];

22 (mm/yy) particular requirements for precast and cast in-situ chambers if differing from the requirements of sub-Clause 507.4 [507.4];

23 particular requirements for corrugated galvanized steel chambers [507.5];

24 (mm/yy) requirements for testing chambers for foul and surface water drains for watertightness [507.8] and carrier, foul and filter drain surveys by Closed Circuit Television (CCTV) [this requirement to be stated in Appendix 90/1 (MCHW 9.5.3)] [509.5];

25 (mm/yy) details of chamber covers, gratings and frames [507.10] and details for special duty covers for use in carriageways [507.18]; requirements for minimum waterway area to gratings for catchpits [507.19]; Polished Skid Resistance Value (PSRV) for chamber covers [507.10];

26 the classes and sizes of cast iron and steel gully gratings [508.4];...

27 requirements for gully gratings if different from the requirements of sub-Clause 508.5;

28 requirements for setting existing covers and gratings to level if different from the requirements of sub-Clauses and 508.8;

29 (mm/yy) whether gullies are to be trapped, untrapped or sumpless [508.1]; details of in situ concrete gullies [508.3];

30 references to drawings showing requirements for filling to pipe bays and verges if different from the requirements of sub-Clause 512.1;

31 requirements for permeable backing if different from the requirements of sub-Clauses 513.1 and 513.2;

32 requirements for the cleaning of chambers, gullies and drains [509.5];

33 (mm/yy) requirements for cleaning of existing drainage systems - Clause 520 [520.1 and 520.4];

34 requirements for rapid setting bedding materials and the locations where they will be required [507.23];

35 (mm/yy) requirements for the cleaning of existing drainage systems using low pressure high volume jetting [521.1]; details of drainage system [521.2] and pipe material [521.3];

36 (mm/yy) limiting distance for deposition of materials referred to in sub-Clauses 503.4, 503.5, 505.4 and 505.5;

37 (mm/yy) requirements for geotextiles [505.3].

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/2: (mm/yy) SERVICE DUCT REQUIREMENTS

NOTE [Note to compiler: This should include:]

1 (mm/yy) details of duct construction [503.7] [cross-reference should be made to HCD drawing no. I2 where appropriate];

2 a schedule of service duct requirements [similar to those in Appendix 5/1 for pipes];

3 (mm/yy) details of permanent marker blocks and location posts required for service ducts [505.9] [crossreference should be made to HCD drawing no. I1 where appropriate].

4 colour coding of ducts [Refer to 501.7, 518.4 and Health and Safety Executive booklet HS(G)47];

5 references to drawings which show chamber types [501.8]

6 duct classification to BS EN 14364 and BS EN 1796 for GRP ducts [Table 5/2]

7 resistance to bending requirements for thermoplastic ducts [Table 5/2]

8 if ducts require water tight joints [504.2]

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/3: SURFACE WATER CHANNELS AND DRAINAGE CHANNEL BLOCKS

1 (mm/yy) [Note to compiler: State here specific requirements cross-referring to the appropriate drawing numbers, including HCD Series B and F drawings as listed in contract specific Appendix 0/4 of the Contract document] [510.1]

2 Requirements for the cross sectional and longitudinal profile of grassed surface water channels 3.3 The duration of protection required from a biodegradable geosynthetic reinforcement used in conjunction with the grassed surface water channel.

4 Requirements for location, profile and gradient drawings of grassed surface water channels.

5 Requirements for drawings locations, reinforcing mesh (BS4483), concrete designation, minimum cover requirements, profile, and hydraulic capacity to be include for combined surface water channel and pipe.

6 Requirements for grass mix [NG 523 23.7]

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/4: FIN DRAINS AND NARROW FILTER DRAINS

NOTE [Note to compiler: This should include:]

1 Permitted alternative types of fin drain and narrow filter drain. [Normally the choice of type of fin or narrow filter drain should be left to the Contractor.]

2 Drawing references showing locations.

3 The maximum permissible O90 determined from the pore size distribution curve of the geotextile [514.4(iv) and 515.3].

4 The permeability of the geotextile [514.4(v) and 515.3].

5 The long term in-plane flow for fin drains [514.5].

6 Pipe diameters [514.10 and 515.6].

7 Trench backfill material for fin drain if not as-dug material [514.9].

8 Category for tolerances at mid-size sieves in Type 8 and Type 9 filter material.[515.5].

9 Permeability of granular material in narrow filter drain where required [515.5].

10 (mm/yy) Maximum drain slope angle if different from 15% [514.10 and 515.6].

11 Dimensions of fin drains and narrow filter drains if different from the requirements of sub-Clauses 514.10 and 515.6 4.12 12 References to drawings and/or schedules which show required levels .

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/5: COMBINED DRAINAGE AND KERB SYSTEMS

NOTE [Note to compiler: Include here:]

1 Drawing references showing locations, etc.

2 Limiting dimensions:

1) (mm/yy) Maximum width and depth of units [if applicable] [516.4].

2) Kerb upstand.

3) Kerb profile [if applicable].

4) (mm/yy) dimensions of side-entry inlets of units to be used in or adjacent to porous asphalt [516.5].

3 (mm/yy) Strength requirements

NOTE [units must be specified as class D or class C. Class D units must be used where there is a possibility of impact from all types of road vehicle that are permitted on trunk roads including motorways. Class C units must only be installed in locations which are protected from direct traffic loading, eg. in areas behind safety barriers. Further advice on other permitted classes can be found in clause 5 of BS EN 1433.] [516.6]

4 (mm/yy) Hydraulic design parameters [516.1 and 516.3]

5 (mm/yy) Any special fittings required [516.10].

6 surveying requirements with pre-cleansing requirements [516.11]

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/6: LINEAR DRAINAGE CHANNEL SYSTEMS

NOTE (mm/yy) [Note to compiler: Include, as appropriate, the various requirements for the prefabricated and the in-situ linear drainage channel systems here:]

1 Drawing references showing locations, etc.

2 Limiting dimensions:

i) (mm/yy) maximum width and depth of units [517.4 and 1103.1]

ii) (mm/yy) dimensions of side-entry inlets of units to be used in or adjacent to porous asphalt [517.5]

3 (mm/yy) Hydraulic design parameters [517.1 and 517.3]

4 (mm/yy) Strength requirements NOTE [units must be specified as class D or class C. Class D units must be used where there is a possibility of impact from all types of road vehicle that are permitted on trunk roads including motorways. Class C units must only be installed in locations which are protected from direct traffic loading, eg. in areas behind safety barriers. Further advice on other permitted classes can be found in clause 5 of BS EN 1433.] [516.6]

5 (mm/yy) Weathering Resistance requirement relating to the grade of weathering resistance for drainage channels made of concrete [see clause 6.3.3.3 of BS EN 1433] [517.7]

6 (mm/yy) Any special fittings required [517.9].

7 survey requirements including pre-cleansing requirements [517.11]

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/7: (mm/yy) THERMOPLASTICS STRUCTURAL WALL PIPES AND FITTINGS

Information to be provided by the Contractor

NOTE The Contractor shall provide the following information, in accordance with sub-Clause 518.2, for the range of pipes and fittings (to be verified by the Certification body - see sub-Clause 518.15):

1 Technical drawings showing dimensions and tolerances including sealing rings and weight per metre, together with properties, as specified in sub-Clauses 518.3 and 518.5.

2 Material specification, as required in sub-clause 518.2:

Table 1 Unplasticised polyvinyl-chloride (PVC-U)

| Property | Test method reference | Specification |
| --- | --- | --- |
| Tensile Properties | BS EN ISO 6259, BS EN ISO 527-1 Vicat BS EN 727 |  |
| Longitudinal reversion | BS EN 743 |  |
| K-value | BS EN 922 |  |
| PVC content | EN 1905 |  |
| Density | BS EN ISO 1183-3, ISO 4451 |  |
| Heat Reversion | ISO 12091 |  |
| Effects of heating (injection moulded fittings only) | BS EN 763 |  |

Table 2 Polyethylene (PE)

| Property | Test method reference | Specification |
| --- | --- | --- |
| Tensile Properties | BS EN ISO 6259, BS EN ISO 527-1 |  |
| Oxygen induction time | BS EN 728 |  |
| Melt Flow Rate | BS EN ISO 1133 |  |
| Density | BS EN ISO 1183-3, ISO 4451 |  |
| Melt Flow Rate | ISO 4440 |  |
| Heat Reversion | ISO 12091 |  |
| Effects of heating (injection moulded fittings only) | BS EN 763 10 |  |

Table 3 Polypropylene (PP)

| Property | Test method reference | Specification |
| --- | --- | --- |
| Tensile Properties | BS EN ISO 6259, BS EN ISO 527-1 |  |
| Oxygen induction time | BS EN 728 |  |
| Melt Flow Rate | BS EN ISO 1133 |  |
| Density | BS EN ISO 1183-3, ISO 4451 |  |
| Heat Reversion | ISO 12091 |  |
| Effects of heating (injection moulded fittings only) | BS EN 763 11 |  |

NG SAMPLE CONTRACT SPECIFIC APPENDIX 5/8: (mm/yy) MAINTENANCE PLANS FOR SOAKAWAYS

NOTE [Compiler to include the following:]

1 Commissioning phase for soakaways.

2 Routine inspections required to determine the rate of accumulation of sediment in soakaways and pre-discharge treatment devices.

3 Timetable for submission of the inspection and maintenance plan(s).